## INDEX
Johan van Sittert Contact Details: Cell - +27 82 563 0988 e-mail: - jvansittert@bbe.co.za BBE tel No: - +27 11 706 9800 | V29
Main Heading | Sub Heading/s
Calendar | Calendar (Enter year)
Planning Tool (New) | Heat and cooling calculations
Planning Graph Calcs 1 | Graph calcs - Heat Flow rate prediction "GEBLER GRAPH" | Graph calcs - Heat Flow rate prediction P959 Env Eng | REJ. Temp. Correction %
Planning Graph Calcs 2 | Graph calcs - Heat Removal capacity of air P956 Env Eng. (18°C NO BAC) | Graph calcs - Heat Removal capacity of air P956 Env Eng. (10°C BAC) | Expected Wet Bulb Temperature | Air cooling capacity
Tons generator | Tunnel Square | Raise bore Round | Panel Rectangular | Holing date Calculator
Refuge Bays | Ref Bay Dist. Calcs | Refuge Bay Requirement Calculator | Refuge Bay Breathable Air Systems | Refuge bay comp air pipe flow calcs | Calculate the hole size diameter for Refuge Bay Chamber valve to achieve pre-set air change | Calculate the heat load of people | Calculate the Qty of air in a pipe | Water tank Calculator (When using a pipe as a water Tank)
Gas | GAS DILUTION | GAS MIXING | GAS Table | Combustibles (LEL and UEL) | Toxins
Airflow | Natural Ventilation Pressure [NVP] No Fans | Natural Ventilation Pressure [NVP] With fans | REYNOLDS NUMBER | CONSERVATION OF ENERGY | Barometric increase with depth | Pressure change with Density Change | Mixing of Airstreams | Quantity change with Density Change | Fraction of Area Open Calculator (Round) | Fraction of Area Open Calculator (Square / Rectangular)
Psychometrics | Cooler Duty 1 | Cooler Duty 2 | Cooling Coils | Water Flow Back Calcs - Coolers | Psychometric QTY - Masflow Calculator | Barometric pressure calculator | Calculate Qty From MF | Substitute climate temperature [tzk] | Water duty Calc | Single density Calc
Thermal Stress | WBGT calculator (Shade) | WBGT calculator (Sunlight) | BMI Calculator | The Substitute climate temperature [tzk]
Comp Air | Pressure Loss through Piping for Air | Air Flow Rate through Piping | Effect of auto compression
Water | Temperature Increase In Pipes | Pump Power Requirements | Pump Efficiency | Fissure Water Calculation
Fans (Graphs + Data) | 4kW fan | 8kW fan | 11kW fan | 15kW fan | 18kW fan | 22kW fan | 45kW fan | 45kW fan | 75kW fan
FAN LAWS | Fan Speed Change - Qty Change | Fan Speed Change - Pressure Change | Fan Speed Change - Power Change | FAN PULLEY SIZE CHANGES | MOTOR PULLEY SIZE CHANGES | Fan Efficiency Calc
Trigonometry & Volume | Right Triangle Solver | Volume Calculator (Square / Rectangular) | Volume Calculator (Round) | Pre Calculated Round Arch and Flat Arched tunnels | Calulating Pipe filled Area
Cost | Cost - Water | Cost - Air | Running Cost -Fan (Known Kw) | Running Cost -(Known Kw) Partial Hours or Shifts | Vent Pipe and Accessories Cost Estimator | Power Saving | Cost per kg/s Refigerated Air Calculator
PLoss Atkins & Resist | ATKINSON’S FORMULA | ATKINSON’S FORMULA Length between fans | Pressure required to overcome frictional resistance | AIR POWER | VELOCITY PRESSURE | DARCY-WEISBACH EQUATION | Motor input power | REGULATORS | Length between fans | K Factors | Velocity in Shaft Calculator | ATKINSON’S FORMULA - Qty Calcs | Vent Hole Dimension Calculator | Shock Loss Calculator | Mentis Grating open area Calc | SHOCK LOSS CALC (Bend)
Stope Calcs | AUI Calculations (All Types)
Dev Calcs | Leakage | Disch Qty Required | PRESSURE LOSS CALCs | K Factors
Dev Qtys | Air Qty Required to meet (Std) Conventional | Air Qty Required to meet (Std) Trackless | Primary Fan requirement to cater for a 2'nd fan - Calculator
Interpolation | Interpolation | Interpolation Multiple data Points
Dust | Number of filter bags required | Rectangular gravity settler | Cylindrical gravity settler | Rectangular gravity settler (2)
DUST Treatment | Initial Application | Maintenance
Stores Req Dev | Ventilation equipment required to ventilate development ends
Heat Calcs | Expected increase in Temp Dev Ends (By M. Symons.) | Auto-compression or de-compression | Virgin rock temperature [approximate] | Virgin rock temperature [Calcs] | Wet kata formula | Amount of Heat transferred (Conduction)
Vent calculator | Tables for quick calcs (Field book)
Flammable gas | Calculation of explosive ranges from gas analysis | Calculation for the egress of gas from an intersection | LEL and UEL of Flammable Gasses (Table)
Air change re-entry | Re-Entry Calculator | Air Change Ventilation Guideline table | Whirly Bird Size and Extraction | BTU Calculator | Re-Entry Calculator - Long Columns
Re-Entry Table
Noise Log ave | Noise Log Ave
Cold Stress | Cold Stress (WCET) OLD Formulae | Cold Stress (WCET) Steadman Formulae | Cold Stress (WCET) Table Formulae 1 | Cold Stress (WCET) Table Formulae 2 | Cold stress related air temperatures report
SCP - Kata - Vel | Development | Stoping | Wet KATA
Unit Conversion | Length, Volume, Molar Flowrate,Volumetrc Flow, Pressure | Power, Energy, Mass, Density, Area | Dynamic Viscosity, Kinematic viscosity, Mass Flowrate, Heat transfer Coefficient, Thermal Conductivity | Heat Flux, Specific Energy, Specific Heat, Temperature
Planning Tool (Old) | Heat and cooling calculations
Trackless Vehicles and Qty Requirements | Trackless Vehicle Data | Vehicle kW Minimum Qty Calculator | Summary of Diesel Ventilation Air Requirements throughout the World | Heat from diesel fuel | Air Volume / Diesel Dilution Table
Vehicle Qty & heat graph
AIRFLOW MEASUREMENT | Pitot tube positions in a circular duct
Waterfall Graph | Waterfall Graph
Refr+BAC+PCT Reports | MONTHLY FRIDGE PLANT PERFORMANCE REPORT | MONTHLY Bulk Air Cooler (BAC) PERFORMANCE REPORT | MONTHLY Pre-Cooling Tower PERFORMANCE REPORT | Refrigeration Plant Health Survey
Changes
Change Index to match Tab Colours
Added Refuge Bay Calcs
Added fraction of area open
Added Trackless Vehicles and Qty Requirements
Added regulator size Calculation
Added BTU - kW Conversion
Added Vehicle Qty & heat graph
Added FAN LAWS
Added Comp Air Calcs
Updated Flammable gas Calculator
added AIRFLOW MEASUREMENT
Added Waterfall Graph
Added Velocity in Shaft Calculator
Add: Area Semi-ellipse
Add Heat from diesel fuel
Add Psychometric QTY - Masflow Calculator
Add Barometric pressure calculator
Add Substitute climate temperature
Add Round ducts at re-entry Calculator
Add Shaft sinking development Qty calculator
Add ATKINSON’S FORMULA - Qty Calcs
Add Primary Fan requirement to cater for a 2'nd fan - Calculator
Add Cost comparison fans
Add Refuge bay comp air pipe flow calcs
Add Calculate the hole size diameter for Refuge Bay Chamber valve to achieve pre-set air change
Add Calculate the Qty of air in a pipe
Added Water tank Calculator (When using a pipe as a water Tank)
Add Gas Table
Add Gas Explosives LEL and UEL table
Add Toxins table
Add Re Entry Table
Add BTU Calculator
Add Whirly Bird Size and Extraction sheet
Updated BP Calculator under Psychometry tab
Add Shock Loss Calculator
Fixed Air Velocity Calc - Kata
Updated Gas Table
Added Reduction of DB Temperatures
Added Dust: Rectangular gravity settler + Cylindrical gravity settler + Rectangular gravity settler (2)
Updated: VELOCITY from VELOCITY PRESSURE (Pitot Tube Readings) Calc Sheet
Add Raise bore Hole / Tunnel (Holing date) Prediction Calculator
Add Cost per kg/s Refigerated Air Calculator
Add Relative Humidity Calc (Single Formulae)
Add velocity to Re-Entry Calculator
Fixed SCP Chart 24.5~25.0
add WATER Duty Calc
Add Mentis Grating open area Calc
Add Noise Log Calculator
Add Themal Stress Tab
Add Fan Efficiency Calc
Add Refr+BAC+PCT Reports TAB
Add Simple Volume Calcs - Pscycrometric tab
Add Density ( w ) - [Single Calc]
Fixed Dewpoint Calc - Louis Matthysen Correction
Fixed WBGT
Fixed Waterflow calc Cooling Coils
Add Re-Entry Calculator - Long Columns
Add Interpolation Multiple data Points
add SHOCK LOSS CALC (Bend)
add Calculating Pipe Fill Area
IF ISBLANK Formula: | IF(ISBLANK(A1),"",Add Your Formula))
CONCATENATE
The horse is sick | The | horse | is | sick
12m³/s | 5 | 7 | m³/s
250 meters | 100 | 150
|  |  |  | 0.57 | m
PI ~ 22/7 | 3.1416 | 3.1416 | Quick circle area calc : Diameter² x 0.7857 | 0.25527 | m²
Date ~ Now | 2026-03-05 09:19 | 2026-03-05 09:19 | 2026-03-05 09:19
üû
OP
Refuge bay comp air pipe flow calc
Calculate the hole size diameter for Refuge Bay Chamber valve to achieve pre-set air change
Calculate the heat load of people
Calculate the Qty of air in a pipe
Water tank Calculator (When using a pipe as a water Tank)
Correcting TXT | Proper Function | lower function | UPPER FUNCTION
AlIGaToR | Aligator | aligator | ALIGATOR
TAG ALLocaTOR BUTTON | Tag Allocator Button | tag allocator button | TAG ALLOCATOR BUTTON
TRUCK riding ON RoAD | Truck Riding On Road | truck riding on road | TRUCK RIDING ON ROAD
The horse IS Sick now | The Horse Is Sick Now | the horse is sick now | THE HORSE IS SICK NOW
Age from ID Number
ID number | Age
6712215888086 | 58
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
Formulas:
Tunnel Square = DATEDIF(DATE(IF(LEFT([Tons generator],2)>TEXT(TODAY(),"YY"),"19"&LEFT([Tons generator],2),"20"&LEFT([Tons generator],2)),MID([Tons generator],3,2),MID([Tons generator],5,2)),TODAY(),"y")

## Calendar
|  | Jan | Apr | Jul | Oct | [6 empty] | Feb | May | Aug | Nov |  |  |  |  | Mar | Jun | Sep | Dec
|  | 2026-01-01 | 2026-04-01 | 2026-07-01 | 2026-10-01 | [5 empty] | 1900-01-27 | 2026-02-01 | 2026-05-01 | 2026-08-01 | 2026-11-01 |  |  |  |  | 2026-03-01 | 2026-06-01 | 2026-09-01 | 2026-12-01
Jan |  | 0 | 0 | 0 | 0 | 1899-12-31 | 0 | 0 | Feb |  | 1899-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | Mar |  | 1899-12-31 | 0 | 0 | 0 | 0 | 0 | 0
Apr |  | 0 | 0 | 0 | 1899-12-31 | 0 | 0 | 0 | May |  | 0 | 0 | 0 | 0 | 0 | 1899-12-31 | 0 | Jun |  | 0 | 1899-12-31 | 0 | 0 | 0 | 0 | 0
Jul |  | 0 | 0 | 0 | 1899-12-31 | 0 | 0 | 0 | Aug |  | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 | Sep |  | 0 | 0 | 1899-12-31 | 0 | 0 | 0 | 0
Oct |  | 0 | 0 | 0 | 0 | 1899-12-31 | 0 | 0 | Nov |  | 1899-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | Dec |  | 0 | 0 | 1899-12-31 | 0 | 0 | 0 | 0
| Enter year for calendar: | [6 empty] | 2026-01-01 |  |  |  |  | CHANGE THE YEAR HERE | [10 empty] | Back to INDEX
(1900 - 2078)
[7 empty] | CALENDER FOR | [7 empty] | 2026 | [11 empty] | Public Holiday- Color Manually
2026
| JANUARY | [8 empty] | FEBRUARY | [8 empty] | MARCH | [7 empty] | 1 January: New Year’s Day
| WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT
| 1 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 21 March: Human Rights Day
| 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |  | 11 | 8 | 9 | 10 | 11 | 12 | 13 | 14
| 3 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |  | 8 | 15 | 16 | 17 | 18 | 19 | 20 | 21 |  | 12 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 3 April: Good Friday *
| 4 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 9 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |  | 13 | 22 | 23 | 24 | 25 | 26 | 27 | 28
| 5 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 29 | 30 | 31 | 0 | 0 | 0 | 0 | 6 April: Family Day
| 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 April: Freedom Day
| JANUARY WK: APRIL |  | MAY | [8 empty] | JUNE
| WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT | 1 May: Workers' Day
| 14 | 0 | 0 | 0 | 1 | 2 | 3 | 4 |  | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
| 15 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 19 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  | 24 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 16 June: Youth Day
| 16 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 20 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  | 25 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 17 | 19 | 20 | 21 | 22 | 23 | 24 | 25 |  | 21 | 17 | 18 | 19 | 20 | 21 | 22 | 23 |  | 26 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 9 August: National Women’s Day
| 18 | 26 | 27 | 28 | 29 | 30 | 0 | 0 |  | 22 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 27 | 28 | 29 | 30 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 31 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 August: Public holiday National Women’s Day observed **
| APRIL WK: JULY |  | AUGUST | [8 empty] | SEPTEMBER | [7 empty] | 24 September: Heritage Day
| WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT
| 27 | 0 | 0 | 0 | 1 | 2 | 3 | 4 |  | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 36 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 16 December: Day of Reconciliation
| 28 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 32 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | 37 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| 29 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |  | 33 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 38 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 25 December: Christmas Day
| 30 | 19 | 20 | 21 | 22 | 23 | 24 | 25 |  | 34 | 16 | 17 | 18 | 19 | 20 | 21 | 22 |  | 39 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| 31 | 26 | 27 | 28 | 29 | 30 | 31 | 0 |  | 35 | 23 | 24 | 25 | 26 | 27 | 28 | 29 |  | 40 | 27 | 28 | 29 | 30 | 0 | 0 | 0 | 26 December: Day of Goodwill
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36 | 30 | 31 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| JULY WK: OCTOBER |  | NOVEMBER | [8 empty] | DECEMBER
| WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT |  | WK | SUN | MON | TUE | WED | THU | FRI | SAT
| 40 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  | 44 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | 48 | 0 | 0 | 1 | 2 | 3 | 4 | 5
| 41 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  | 45 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |  | 49 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| 42 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |  | 46 | 15 | 16 | 17 | 18 | 19 | 20 | 21 |  | 50 | 13 | 14 | 15 | 16 | 17 | 18 | 19
| 43 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 47 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |  | 51 | 20 | 21 | 22 | 23 | 24 | 25 | 26
| 44 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | 48 | 29 | 30 | 0 | 0 | 0 | 0 | 0 |  | 52 | 27 | 28 | 29 | 30 | 31 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Formulas:
Apr = [Mar]+31
Jul = [Jun]+30
Oct = [Sep]+30
Feb = [Jan]+31
May = [Apr]+30
Aug = [Jul]+31
Nov = [Oct]+31
Mar = [Feb]+L2
Jun = [May]+31
Sep = [Aug]+31
Dec = [Nov]+30
Note on I8: Enter first Day Month and year of new year Eg: 01 Jan 2016 in the following format: 2016/01/01

## Planning Tool (New)
HEAT AND COOLING CALCULATIONS
| INPUTS | Year 1 | Section 1 | [5 empty] | Section 2 | [5 empty] | Section 3 | [5 empty] | Back to INDEX
| VENTILATION DISTRICT | TOT/AVE | PLAN |  | AIR |  | KT |  | PLAN |  | AIR |  | KT |  | PLAN |  | AIR |  | KT
E | MONTHLY PROD. RATE IN KT/MONTH STOPING | 123.9364 | 0.33637 |  | 0.33637 |  | 4028.0491 | 4028.0491 | 3.6 |  | 3.6 |  | 1.4021 | 1.4021 | 120 |  | 120 |  | 38.0663 | 38.0663
F | MONTHLY PROD. RATE IN KT/MONTH DEV. | 0 |  |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  |  | m³/sec |  | Kg/sec | w (Density)
| TOTAL PRODUCTION DEV+STOPING KT/MONTH | 123.9364 | 0.33637 | 0 | 0.33637 | 0 | 4028.0491 | 4028.0491 | 3.6 | 0 | 3.6 | 0 | 1.4021 | 1.4021 | 120 | 0 | 120 | 0 | 38.0663 | 38.0663 |  |  | U/C # | 0
M | MEAN ROCK BREAKING DEPTH IN METERS |  | 560 |  | 560 |  | 560 |  | 2974 |  | 2974 |  | 2974 |  | 3100 |  | 3100 |  | 3100 |  |  |  |  | 0
N | AVE. DIST. FROM THE SHAFT IN METERS |  | 1400 |  | 1400 |  | 1400 |  | 3299 |  | 3299 |  | 3299 |  | 3500 |  | 3500 |  | 3500 |  |  |  |  | 0
| NO. OF LOCOMOTIVES (BASED UPON KW/Kt) |  | 4 | 10 | 4 | 10 | 4 | 10 | 20 | 10 | 20 | 10 | 20 | 10 | 20 | 10 | 20 | 10 | 20 | 10 |  |  |  | 0
| NO. OF MEN (BASED UPON KW/Kt) |  | 0.2 | 3 | 0.2 | 3 | 0.2 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 |  |  | # System | 0
| ACTUAL HEAT FROM ELECTRICAL ENERGY KW/Kt |  |  | 10 | 0 | 10 | 0 | 10 | 250 | 10 | 250 | 10 | 250 | 10 | 125 | 10 | 125 | 10 | 125 | 10 |  | Avail = |  | Avail =
| AIR VOLUME (EXCLUDING LEAKAGE) IN M3/S | 2627 | 1967 |  | 0.17485 |  | 1967 |  | 60 |  | 56.3147 |  | 60 |  | 600 |  | 2973.6489 |  | 600 |  | 2627 | 0 | -2627 | 0
| Air volume ONLY Used for Development |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| REQUIRED M/FLOW AT (Input Value C14) KG/S/KT |  | 1.5137 | 0 | 1.5137 | 0 | 18126.2209 | 18126.2209 | 17.64 | 0 | 17.64 | 0 | 6.8702 | 6.8702 | 588 | 0 | 588 | 0 | 186.5249 | 186.5249
| DESIGN AIR KG/S/KT |  | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
| DESIGN WATER TONNE/TONNE |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
| Fisure Water @0.4 t/ton/month |  | 0.01 | [5 empty] | 0.4 | [5 empty] | 0.4
| SERVICE WATER USED FOR COOLING Y=1 N=0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Surface air / Mix Temperature (Usually 10°C) |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 |  |  | 141.5
| Service Water Availability (l/s) |  | 1 | 1 |  |  |  | 1 | 16 | 16 |  |  |  | 16 |  | 0 |  |  |  | 0
| DESIGN COOL. CAR DELTA WATER TEMPERATURE |  |  | 0 | 0 | 0 | 0 |  | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14
| DESIGN WATER DELTA TEMPERATURE OF SERVICE WATER |  | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| SECTION AIR UTILIZATION IN % |  | 100 | 100 | 100 | 100 | 100 | 100 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| Geothemal gradient (Eg.: 0.0113) |  | 0.022 |  | 0.022 |  | 0.022 |  | 0.0113 |  | 0.022 |  | 0.022 |  | 0.022 |  | 0.022 |  | 0.022 |  | Refrigeration l/s Total
| Geothemal gradient (Eg.: 21°) |  | 21.5 |  | 21.5 |  | 21.5 |  | 21 |  | 21.5 |  | 21.5 |  | 21.5 |  | 21.5 |  | 21.5 |  |  | Avail =
| Surface BP |  | 83 | 83 |  | 83 |  | 83 | 87.5 | 87.5 |  | 87.5 |  | 87.5 | 83 | 83 |  | 83 |  | 83 | #DIV/0! | 120 | 12.5299
| Fissure Water ( 0.4t/ton/m) |  | 0.01 |  | 0.01 | 0.01 | 0.01 |  | 0.4 |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
| Density |  | 1.2 |  | 1.2 |  | 1.2 |  | 1.3 |  | 1.3 |  | 1.3 |  | 1.3 |  | 1.3 |  | 1.3
| DESIGN REJECT TEMP WB IN DEG. C |  | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
OUTPUTS
ANALYSIS OF BEST COMBINATION
| HEAT PROD. RATE IN WATTS/TONNE/MONTH |  | 56.0178 |  | 52.4173 |  | 52.4173 |  | 255.9044 |  | 540.6485 |  | 540.6485 |  | 581.7301 |  | 577.1636 |  | 577.1636
| REJ. TEMP. CORRECTION PERCENT |  | -0.02 |  | -0.02 |  | -0.02 |  | 0.06 |  | 0.06 |  | 0.06 |  | 0.06 |  | 0.06 |  | 0.06
| HEAT PROD. RATE CORRECTED FOR TEMP. |  | 54.8975 |  | 51.369 |  | 51.369 |  | 271.2587 |  | 573.0874 |  | 573.0874 |  | 616.6339 |  | 611.7934 |  | 611.7934
| VRT °C = |  | 33.82 |  | 33.32 |  | 33.32 |  | 54.6062 |  | 86.428 |  | 86.428 |  | 89.7 |  | 89.2 |  | 89.2
| Heat load fissure water kW |  | 0.017793 |  | 0.015113 |  | 180.9762 |  | 59.8941 |  | 132.9011 |  | 51.7603 |  | 4680.263 |  | 4642.0256 |  | 1472.5397
G | HEAT PRODUCTION IN KW FOR ROCK kW | 98722.6539 | 19.8967 | 94.8291 | 18.7071 | 94.8291 | 224015.5294 | 94.8291 | 2026.4254 | 15.0486 | 3186.0156 | 15.0486 | 1240.8404 | 15.0486 | 96676.3317 | 36.6456 | 96057.2355 | 36.6456 | 30471.2012 | 36.6456
L | MASSFLOW OF AIR | 3218.4 | 2360.4 | 82.256 | 0.20982 | 82.256 | 2360.4 | 82.256 | 78 | 27.1438 | 73.2091 | 27.1438 | 78 | 27.1438 | 780 | 24.67 | 3865.7436 | 24.67 | 780 | 24.67 | 3218.4
H | HEAT REMOVAL CAPACITY OF AIR IN KW WITH BAC | 253591.9456 | 223834.5532 | 49.566 | 19.8967 | 49.566 | 223834.5532 | 49.566 | 1173.7924 | -4.3037 | 1101.6955 | -4.3037 | 1173.7924 | -4.3037 | 28583.6 | -6.4667 | 141662.6517 | -6.4667 | 28583.6 | -6.4667 | 223834.5532
K | SERVICE WATER L/S | 107.4701 | 0.17844 | 0.48225 | 0.17844 | 0.48225 | 2136.793 | 0.48225 | 3.125 | 0.48225 | 3.125 | 0.48225 | 1.2171 | 0.48225 | 104.1667 | 0.48225 | 104.1667 | 0.48225 | 33.0437 | 0.48225 | l/s Total Req
| Total Water L/S Required |  | 0.17844 |  | 0.17844 |  | 2136.793 |  | 3.125 |  | 3.125 |  | 1.2171 |  | 104.1667 |  | 104.1667 |  | 33.0437 |  | 107.4701
I | HEAT REM. CAP. OF SERV. WATER IN KW |  | 0 | 0 | 0 | 0 | 0 | 0 | 39.2531 | 6.0576 | 39.2531 | 6.0576 | 15.2877 | 6.0576 | 1308.4375 | 6.0576 | 1308.4375 | 6.0576 | 415.0615 | 6.0576
J | HEAT REM. CAP. OF BULK COOL. IN KW. |  | 0
HEAT REM. CAP. OF COOL. CARS IN KW
| TOTAL REFRIG. AVAILABLE IN KW | 1347.6906 | 0 |  | 0 |  | 0 |  | 39.2531 |  | 39.2531 |  | 15.2877 |  | 1308.4375 |  | 1308.4375 |  | 415.0615
| TOTAL RESOURCES AVAILABLE IN KW | 254939.6362 | 223834.5532 |  | 19.8967 |  | 223834.5532 |  | 1213.0455 |  | 1140.9486 |  | 1189.0801 |  | 29892.0375 |  | 142971.0892 |  | 28998.6615
QUANTITY REQUIRED TO ACHIEVE DESIGN
| WETBULB TEMPERATURE WITH BAC | 3030.1384 | 0.17485 | 1.2 | 0.18952 | 1.2 | 2269.4953 | 1.2 | 56.3147 | 1.3 | 89.1764 | 1.3 | 34.7311 | 1.3 | 2973.6489 | 1.3 | 2954.345 | 1.3 | 937.175 | 1.3 | 1.1997
| ACT. MASSFLOW OF AIR PER KTONNE |  | 7017.1683 |  | 0.62376 |  | 0.58599 |  | 21.6667 |  | 20.3359 |  | 55.6319 |  | 6.5 |  | 32.2145 |  | 20.4906
| HEAT PROD. RATE LESS TOTAL RESOURCES | -156216.9823 | -223814.6565 |  | -1.1896 |  | 180.9762 |  | 813.3799 |  | 2045.067 |  | 51.7603 |  | 66784.2942 |  | -46913.8537 |  | 1472.5397
| Refrigeration kW REQ. TO ACHIEVE REJ. WB TEMP. |  | 0 |  | 0 |  | 180.9762 |  | 813.3799 |  | 2045.067 |  | 51.7603 |  | 66784.2942 |  | 0 |  | 1472.5397
| WATER Flow l/s REQ. TO ACHIEVE REJ. WB TEMP. |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | 13.8759 |  | 34.888 |  | 0.88301 |  | 1139.3138 |  | 0 |  | 25.1209
ADDITIONAL CALCULATIONS
| POT. Kt AT 4KG/S/Kt THAT CAN BE MINED IN AREA | 804.6 | 590.1 | 23.7073 | 0.052454 | 23.7073 | 590.1 | 23.7073 | 19.5 | 3.7622 | 18.3023 | 3.7622 | 19.5 | 3.7622 | 195 | 9.1614 | 966.4359 | 9.1614 | 195 | 9.1614
| ACTUAL PLANNED CENTARES | 29720.9532 | 80.6655 | 0 | 80.6655 | 0 | 965959.0128 | 965959.0128 | 863.3094 | 0 | 863.3094 | 0 | 336.2285 | 336.2285 | 28776.9784 | 0 | 28776.9784 | 0 | 9128.6106 | 9128.6106
| POTENTIAL CENTARES IF AIR IS USED FOR M² | 192949.6403 | 141510.7914 | 5685.1965 | 12.5789 | 5685.1965 | 141510.7914 | 5685.1965 | 4676.259 | 902.1955 | 4389.0329 | 902.1955 | 4676.259 | 902.1955 | 46762.5899 | 2196.9809 | 231759.2077 | 2196.9809 | 46762.5899 | 2196.9809
| POT. Kt STOPING BASED ON TOT. RESOURCES | 3828.7612 | 3787.5492 | 0 | 0.35805 | 0 | 4028.0491 | 0 | 2.2206 | 0 | 1.3453 | 0 | 1.4021 | 0 | 38.9913 | 0 | 187.677 | 0 | 38.0663 | 0
| POT. M² BASED ON TOT. RESOURCES | 918168.1439 | 908285.1887 | 0 | 85.8643 | 0 | 965959.0128 | 0 | 532.5283 | 0 | 322.6186 | 0 | 336.2285 | 0 | 9350.4269 | 0 | 45006.4705 | 0 | 9128.6106 | 0
| M/FLOW ALLOWED FOR STOPING FOR DESIGN WB | 2413.8 | 1770.3 | 71.1218 | 0.15736 | 71.1218 | 1770.3 | 71.1218 | 58.5 | 11.2865 | 54.9068 | 11.2865 | 58.5 | 11.2865 | 585 | 27.4842 | 2899.3077 | 27.4842 | 585 | 27.4842
| M/FLOW ALLOWED FOR DEV. FOR DESIGN WB | 804.6 | 590.1 | 23.7073 | 0.052454 | 23.7073 | 590.1 | 23.7073 | 19.5 | 3.7622 | 18.3023 | 3.7622 | 19.5 | 3.7622 | 195 | 9.1614 | 966.4359 | 9.1614 | 195 | 9.1614
| ACTUAL TOTAL RESOURCES AVAIL. PER KILOTONNE | 666017.6536 | 665431.5962 |  | 59.1504 |  | 55.569 | 0 | 336.9571 |  | 316.9302 |  | 848.0874 | 0 | 249.1003 |  | 1191.4257 |  | 761.7934 | 0
Note on F3: Johan van Sittert: How much air do you require to mine the volume
Note on H3: Johan van Sittert: How much mining volume can you do with the air you have available
Note on L3: Johan van Sittert: How much air do you require to mine the volume
Note on N3: Johan van Sittert: How much mining volume can you do with the air you have available
Note on R3: Johan van Sittert: How much air do you require to mine the volume
Note on T3: Johan van Sittert: How much mining volume can you do with the air you have available
Note on D4: Fill all Fields (White )
Note on J4: Fill all Fields (White )
Note on D32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on F32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on H32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on J32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on L32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on N32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on P32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on R32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on T32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on D33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on F33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on H33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on J33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on L33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on N33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on P33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on R33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on T33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on D34: MSymons: formula correct Checked H Nourse J v Sittert
Note on F34: MSymons: formula correct Checked H Nourse J v Sittert
Note on H34: MSymons: formula correct Checked H Nourse J v Sittert
Note on J34: MSymons: formula correct Checked H Nourse J v Sittert
Note on L34: MSymons: formula correct Checked H Nourse J v Sittert
Note on N34: MSymons: formula correct Checked H Nourse J v Sittert
Note on P34: MSymons: formula correct Checked H Nourse J v Sittert
Note on R34: MSymons: formula correct Checked H Nourse J v Sittert
Note on T34: MSymons: formula correct Checked H Nourse J v Sittert
Note on D35: MSymons: formula correct Checked H Nourse J v Sittert
Note on F35: MSymons: formula correct Checked H Nourse J v Sittert
Note on H35: MSymons: formula correct Checked H Nourse J v Sittert
Note on J35: MSymons: formula correct Checked H Nourse J v Sittert
Note on L35: MSymons: formula correct Checked H Nourse J v Sittert
Note on N35: MSymons: formula correct Checked H Nourse J v Sittert
Note on P35: MSymons: formula correct Checked H Nourse J v Sittert
Note on R35: MSymons: formula correct Checked H Nourse J v Sittert
Note on T35: MSymons: formula correct Checked H Nourse J v Sittert
Note on D37: MSymons: formula correct Checked H Nourse J v Sittert
Note on E37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on F37: MSymons: formula correct Checked H Nourse J v Sittert
Note on G37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on H37: MSymons: formula correct Checked H Nourse J v Sittert
Note on I37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on J37: MSymons: formula correct Checked H Nourse J v Sittert
Note on K37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on L37: MSymons: formula correct Checked H Nourse J v Sittert
Note on M37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on N37: MSymons: formula correct Checked H Nourse J v Sittert
Note on O37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on P37: MSymons: formula correct Checked H Nourse J v Sittert
Note on Q37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on R37: MSymons: formula correct Checked H Nourse J v Sittert
Note on S37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on T37: MSymons: formula correct Checked H Nourse J v Sittert
Note on U37: Air Cooling Power KJ/kg Heat Removal Capacity of air (WITH BAC Operating as an input "Surface Air Mixture") =E42-(D18-18)*(E41-E42)/8 New formula Developed Nov 2011 Manupulated from Heat Removal Graph "y=mx+c"
Note on D38: MSymons: formula correct Checked H Nourse J v Sittert
Note on E38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on F38: MSymons: formula correct Checked H Nourse J v Sittert
Note on G38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on H38: MSymons: formula correct Checked H Nourse J v Sittert
Note on I38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on J38: MSymons: formula correct Checked H Nourse J v Sittert
Note on K38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on L38: MSymons: formula correct Checked H Nourse J v Sittert
Note on M38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on N38: MSymons: formula correct Checked H Nourse J v Sittert
Note on O38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on P38: MSymons: formula correct Checked H Nourse J v Sittert
Note on Q38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on R38: MSymons: formula correct Checked H Nourse J v Sittert
Note on S38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on T38: MSymons: formula correct Checked H Nourse J v Sittert
Note on U38: New Formula Nov 2011 Air Cooling Capacity Surface air at 5°C
Note on E39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on G39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on I39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on K39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on M39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on O39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on Q39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on S39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on U39: New Formula Nov 2011 Air Cooling Capacity Surface air at 18°C
Note on D40: Formula correct Checked H Nourse J v Sittert
Note on E40: Factor To get to 1000 / sec per 24 shifts
Note on F40: Formula correct Checked H Nourse J v Sittert
Note on G40: Factor To get to 1000 / sec per 24 shifts
Note on H40: Formula correct Checked H Nourse J v Sittert
Note on I40: Factor To get to 1000 / sec per 24 shifts
Note on J40: Formula correct Checked H Nourse J v Sittert
Note on K40: Factor To get to 1000 / sec per 24 shifts
Note on L40: Formula correct Checked H Nourse J v Sittert
Note on M40: Factor To get to 1000 / sec per 24 shifts
Note on N40: Formula correct Checked H Nourse J v Sittert
Note on O40: Factor To get to 1000 / sec per 24 shifts
Note on P40: Formula correct Checked H Nourse J v Sittert
Note on Q40: Factor To get to 1000 / sec per 24 shifts
Note on R40: Formula correct Checked H Nourse J v Sittert
Note on S40: Factor To get to 1000 / sec per 24 shifts
Note on T40: Formula correct Checked H Nourse J v Sittert
Note on U40: Factor To get to 1000 / sec per 24 shifts
Note on D42: Formula correct Checked H Nourse J v Sittert
Note on F42: Formula correct Checked H Nourse J v Sittert
Note on H42: Formula correct Checked H Nourse J v Sittert
Note on J42: Formula correct Checked H Nourse J v Sittert
Note on L42: Formula correct Checked H Nourse J v Sittert
Note on N42: Formula correct Checked H Nourse J v Sittert
Note on P42: Formula correct Checked H Nourse J v Sittert
Note on R42: Formula correct Checked H Nourse J v Sittert
Note on T42: Formula correct Checked H Nourse J v Sittert
Note on D51: Johan van Sittert:

## Planning Graph Calcs 1
Back to INDEX
Graph calcs - Heat Flow rate prediction P959 Env Eng
Distance from Shaft in m |  | 2000 | m | Enter
Virgin Rock Temperature |  | 56.8 | °C | Enter
Heat Production kW per kton / month |  | 238.5314 | kW/kt/m
HEAT PROD. RATE CORRECTED FOR TEMP. |  | 262.3846 | kW/kt/m
Graph calcs - Heat Flow rate prediction "GEBLER GRAPH"
Distance from Shaft in m |  | 2000 | m | Enter
Virgin Rock Temperature |  | 56.8 | °C | Enter
Heat Production kW per kton / month |  | 238.5704 | kW/kt/m
HEAT PROD. RATE CORRECTED FOR TEMP. |  | 262.4274 | kW/kt/m
REJ. Temp. Correction %
Design Wetbulb Temperature |  | 27.5 | °C | Enter
Temp. Correction % |  | 10 | %
10%
Notes
1. 50% of losses is added as cooling (Horizontal - insulation etc.)
2. (10-12%) 11% of total cooling is lost
3.
4.
5.
6.

## Waterfall Graph
Back to INDEX
HEAT LOAD
Description | Value | % |  |  |  |  | Base | Fall | Rise
Surrounding rock | 8850 | 21.13% |  |  |  | Surrounding rock | 8850 | 0 | 8850 | 8850
Other heat loads | 3160 | 7.544% |  |  |  | Other heat loads | 8850 | 0 | 3160 | 3160
Auto-compression | 16800 | 40.11% |  |  |  | Auto-compression | 12010 | 0 | 16800 | 16800
Auxiliary fans + Electrical Energy | 500 | 1.194% |  |  |  | Auxiliary fans + Electrical Energy | 28810 | 0 | 500 | 500
Broken Rock | 9600 | 22.92% |  |  |  | Broken Rock | 29310 | 0 | 9600 | 9600
TMM Fleet | 2975 | 7.103% |  |  |  | TMM Fleet | 38910 | 0 | 2975 | 2975
| 41885 | 100% |  |  |  | Refrigeration | 23300 | 27000 | 0 | 27000
COOLING | [5 empty] | Air cooling power | 23300 | 23300 | 0 | 23300
Description | Value | %
Refrigeration | 27000 | 53.68%
Air cooling power | 23300 | 46.32%
| 50300 | 100%
"Field calculator" Quick Heatload and Airflow Calculator | [5 empty] | Reject |  |  | Intake |  |  | Auto Compr
Where: | [5 empty] | Wet Bulb Temp °C | 26.6 | °C | Wet Bulb Temp °C | 22.3 | °C | Wet Bulb Temp °C | 26.6 | °C
Start Air Temperature Surface WB |  | 22.3 | °C WB |  |  | Dry Bulb Temp °C | 34 | °C | Dry Bulb Temp °C | 25.1 | °C | Dry Bulb Temp °C | 34 | °C
Start Air Temperature Surface DB |  | 25.1 | °C DB |  |  | BP | 93.11 | KPa | BP | 83 | KPa | BP | 93.11 | KPa
Surface Intake air temp mix (BAC + Ambient air mix temp) |  | 22.3 | °C WB |  |  | Vapour Press (Pw) | 3.0371 | KPa | Vapour Press (Pw) | 2.5417 | KPa | Vapour Press (Pw) | 3.0371 | KPa
Surface Intake air temp mix (BAC + Ambient air mix temp) |  | 25.1 | °C DB |  |  | Moisture Content ( r ) | 0.020973 | g/Kg | Moisture Content ( r ) | 0.019649 | g/Kg | Moisture Content ( r ) | 0.020973 | g/Kg
Barometric Pressure Surface |  | 83 | kPa | BP Link |  | Moisture Content ( g/Kg ) | 20.9727 | g/Kg | Moisture Content ( g/Kg ) | 19.649 | g/Kg | Moisture Content ( g/Kg ) | 20.9727 | g/Kg
Barometric Pressure Underground (Mean) |  | 93.11 | kPa |  |  | Specific Volume ( v ) | 0.97867 | m³/Kg | Specific Volume ( v ) | 1.0639 | m³/Kg | Specific Volume ( v ) | 0.97867 | m³/Kg | Nth Ramp | Sth Ramp | Levels
Depth Below surface |  | 590 | m |  |  | Density ( w ) | 1.0432 | Kg/m³ | Density ( w ) | 0.95843 | Kg/m³ | Density ( w ) | 1.0432 | Kg/m³ | Length | Length | Length
Workings Mean Distance From Shaft |  | 1400 | m |  |  | Enthalpy ( H ) | 87.9061 | Kj/Kg | Enthalpy ( H ) | 75.2553 | Kj/Kg | Enthalpy ( H ) | 93.6822 | Kj/Kg | m | m | m
Rock Specific Heat |  | 960 | j/kg°C |  |  | Sigma Heat ( S ) | 85.5742 | Kj/Kg | Sigma Heat ( S ) | 73.4237 | Kj/Kg | Sigma Heat ( S ) | 91.3503 | Kj/Kg | 48 | 35 | 15
k Tons produced |  | 194 | kt/mth |  |  | Relative Humidity | 57.1241 | % | Relative Humidity | 79.7982 | % | Relative Humidity | 57.1241 | % | 13 | 31 | 10
Reject Design Temperature (WB) |  | 26.6 | °C WB |  |  | Dew point Temp °Cerature ( tdp ) | 15.3047 | °C | Dew point Temp °Cerature ( tdp ) | 13.5092 | °C | Dew point Temp °Cerature ( tdp ) | 15.3047 | °C | 23 | 175 | 167
Reject Design Temperature (DB) |  | 34 | °C DB | [8 empty] | Auto Compression increase | 5.7761 | Kj/Kg | 15 | 31 | 52
Estimated BAC airflow Volume |  | 0 | m³/s |  |  | BAC | [8 empty] | 12 | 16 | 30
Geothermal gradient (Eg.: 21,27°) |  | 23.9 | °C |  |  | Wet Bulb Temp °C | 22.3 | °C |  |  |  | Delta Sigma Heat | 12.1505 |  | 27 | 12 | 66
Geothermal gradient |  | 0.0192 | °C/m |  |  | Dry Bulb Temp °C | 25.1 | °C | [6 empty] | 17 | 66.3 | 28
Fissure Water |  | 0.04 | kW/kt |  |  | BP | 83 | KPa | [6 empty] | 13.5 | 104.5 | 10
Total Production Vehicle kW |  | 1 | kW | 1.5 |  | Vapour Press (Pw) | 2.5417 | KPa | [6 empty] | 9.1 | 15.8 | 35
Vehicle Heatload factor @ 1.5X / 2X / 3X |  | 1.5 |  |  |  | Moisture Content ( r ) | 0.019649 | g/Kg | [6 empty] | 53.3 | 17.2 | 121
Total Services Vehicle kW |  | 1 | kW | 2 |  | Moisture Content ( g/Kg ) | 19.649 | g/Kg | [6 empty] | 27.1 | 15.7 | 48
Vehicle Heatload factor @ 0.5 |  | 2 |  |  |  | Specific Volume ( v ) | 1.0639 | m³/Kg | [6 empty] | 32.1 | 36.2 | 10
UG Electrical energy consumed (Estimate) |  | 880 | kW |  |  | Density ( w ) | 0.95843 | Kg/m³ | [6 empty] | 18.7 | 66.6 | 42
Electrical energy % as heat (Usually 5-10%) |  | 7% | % |  |  | Enthalpy ( H ) | 75.2553 | Kj/Kg | [6 empty] | 13.5 | 15.8 | 24
Or…. Electrical energy kW/kt (Usually ±25kW/kt) |  | 0 | kW/kt |  |  | Sigma Heat ( S ) | 73.4237 | Kj/Kg | [6 empty] | 15.4 | 15.7 | 17
Quantity of Air (Main fan volume) |  | 1967 | m³/s |  |  | Relative Humidity | 79.7982 | % | [6 empty] | 62.5 | 15.8 | 52
Density ( w ) |  | 1.0432 | Kg/m³ |  |  | Dew point Temp °Cerature ( tdp ) | 13.5092 | °C | [6 empty] | 38.8 | 15.7 | 18
Mass flow |  | 2052.0137 | Kg/s |  |  | BAC Duty | 0 | kW | [6 empty] | 25.5 | 8 | 13
VRT |  | 35.228 | °C | [11 empty] | 13.2 | 43.8 | 24
Sigma Heat Air IN at … | 22.3 | 73.4237 | Kj/Kg | [11 empty] | 13.6 | 59.2 | 77
Sigma Heat Air Air OUT at ... (Reject Temp) | 26.6 | 85.5742 | Kj/Kg |  |  | Estimate Heat from Broken rock (Quick Calc) | [8 empty] | 19.6 | 15.7 | 28
Auto compression |  | 5.7761 | °C | [11 empty] | 9.2 | 15.8 | 42
Auto compression Sigma Heat |  | 91.3503 | Kj/Kg |  |  | Rock produced | 1.05 | kt/day | [6 empty] | 62.4 | 4.1 | 89
Mine Linear heat |  | 75.1542 | kW/kt/m |  |  | Rock produced | 1050 | t.day | [6 empty] | 32.9 | 17.2 | 40
Air Cooling Power |  | 22673.5552 | kW |  |  | Hours | 16 | hours | [6 empty] | 30.5 | 8 | 61
Heat from rock |  | 78.9119 | kW |  |  | Specific Heat of rock | 0.825 | kJ/kg. | Typical valure 0.600-0.920 | [5 empty] | 23.4 | 26 | 87
Heat from Broken rock |  | 129.757 | kW |  |  | Rock produced (kg/s) | 18.2292 | kg/s | [6 empty] | 14.3 | 90.8 | 62
Heat from electrical energy i.e.: Fans, Subs |  | 61.6 | kW |  |  | VRT | 35.228 | °C | [6 empty] | 17.9 | 18.2 | 7
Total Vehicle kW |  | 3.5 | kW |  | l/s | Heat from Rock | 8.628 | °C | [6 empty] | 61.4 | 16.9 | 74
Auto compression Heat Generated |  | 11852.6365 | kW |  |  | Reject Temp | 26.6 | °C | [6 empty] | 69.7 | 13.3 | 16
Fissure Water Heat Generated |  | 106.6718 | kW | 2.9528 |  | Heat from Rock (kW) | 129.757 | kW | [6 empty] | 9.1 | 40.9 | 7
Total HEATLOAD |  | 12233.0771 | kW | [11 empty] | 17.9 | 79.2 | 10
Heat Removal Capacity of Air In kW (BAC Used) |  | 22673.5552 | kW | [11 empty] | 19.6 | 17.8 | 53
TOTAL Refrigeration Required ("+"=Surplus "-"=Shortfall) |  | 10440.4781 | kW | [11 empty] | 9.1 | 9.2 | 18
Airflow Required | [14 empty] | 9.7 | 15 | 37
REQUIRED M/FLOW rate Kg/s/Kt (Include losses and commitments) |  | 4.5 | Kg/s/Kt |  |  | TMM Fleet | Heat Load Factor (Guide) | [7 empty] | 49.3 | 11.9 | 18
REQUIRED M/Flow Kg/s/Kt |  | 873 | Kg/s |  |  | Dump Trucks | 2 | 1.5 | [6 empty] | 52.4 | 35.4 | 16
Diesel Fleet dilution factor |  | 0.06 | m³/s/rated kW diesel power |  |  | LHDs | 1.5 | 1.2 | [6 empty] | 11.1 | 81 | 6
Diesel fleet usage |  | 70% |  |  |  | Services vehicles | 0.5 | [7 empty] | 17 | 18.1 | 21
REQUIRED Qty Based on Diesel Fleet |  | 0.084 | m³/s | [11 empty] | 8 | 23.3 | 20
Quantity of Air Required ~ Based on Kg/s/Kt |  | 976.5121 | m³/s |  |  | Linear Heat from rock Conv Belt |  |  |  |  | Conv Belt Inputs |  |  |  | 13.7 | 13.6 | 83
Quantity of Air Required Based on Diesel Fleet |  | 0.084 | m³/s | [7 empty] | tpd | 32000 |  |  | 17.9 | 13.7 | 52
Airflow required on Surface |  | 0.091432 | m³/s |  |  | Rock produced | 32 | kt/day |  |  | tpa | 9984000 | 10000000 | Million tpa | 60.1 | 66.4 | 23
Mass flow of Air Required Based on Diesel Fleet |  | 0.08763 | Kg/s |  |  | Rock produced | 32000 | t.day |  |  | kg | 32000000 | 833333.3333 | = tpm | 9 | 37.6 | 83
Airflow required Density Change |  | -0.0074315 |  |  |  | Hours | 16 | hours |  |  | Shifts / mth | 26 | 27777.7778 | = tpd
Leakage - 10% |  | 0.011886 | m³/s | 0.13 |  | Specific Heat of rock | 0.825 | kJ/kg. | Typical valure 0.600-0.920 |  | kt/day | 32 |  |  | 17.4 | 17.5 | 123
Ancillary vent - 20% |  | 0.0027429 | m³/s | 0.03 |  | Rock produced (kg/s) | 555.5556 | kg/s |  |  | kg/s | 555.5556 |  |  | 62 | 17.4 | 43
TOTAL AIRFLOW REQUIRED ~ Based on Diesel fleet |  | 0.10606 | m³/s |  |  | VRT | 54 | °C | [6 empty] | 48 | 19.6 | 54
Airflow Primary Infrastructure Required | [5 empty] | Rock exposure on conveyor | 50% | % |  |  | Potential energy gain |  |  |  | 21.7 | 10.5 | 72
REQUIRED Intake Shaft velocity |  | 12 | m/s |  |  | Heat from Rock | 27 | °C |  |  | Pr | 555.5556 | m |  | 9.6 | 29.7 | 22
Shaft area required |  | 81.376 | m² |  |  | Belt DB intake Temp | 36.5 | °C | 17.5 |  | g | 9.79 |  |  | 22.1 | 79.2 | 41
Intake Shaft Diameter |  | 10.179 | m Diameter |  |  | Heat from Rock (kW) | 8020.8333 | kW | 9.5 |  | ΔH | -485 |  |  | 9.1 | 8.8 | 45
REQUIRED Return Shaft velocity |  | 22 | m/s |  |  | 50% Exposure kW | 4010.4167 | kW |  |  | kW | -2637.8611 |  |  | 55.2 | 9.2 | 66
Shaft area required |  | 44.3869 | m² |  |  | Linear Heat Broken Rock | 0.99023 | kW/m | [6 empty] | 58.6 | 23.3 | 29
Return Shaft Diameter |  | 7.5177 | m Diameter |  |  | 50% | 4010.4167 | kW | [6 empty] | 7.9 | 13.6 | 11
Water flow infrastructure Required | [10 empty] | tpm | 32000 |  |  | 17.8 | 13.8 | 21
BAC Delta temperature |  | 18 | °C | [7 empty] | tpd | 1051.3347 |  |  | 13.4 | 76.3 | 30
BAC Water Requirements |  | 0 | l/s |  |  | Conv Belt Electrical Equipment |  |  |  |  | kt/day | 1.0513 |  |  | 31.5 | 29.6 | 57
Cooling water Delta temperature (Reject temp - Plant out water temp) |  | 23 | °C |  |  | Conveyor 1 | 1905 | kWE | [6 empty] | 24.4 | 8.9 | 29
Underground Cooling Water Requirement |  | -108.4151 | l/s |  |  | Conveyor 2 | 85 | kWE | [6 empty] | 52.3 | 8.9 | 65
Water flow Required Ton per Ton |  | 0.5 | t/t |  |  | Conveyor 3 | 1905 | kWE | [6 empty] | 19.4 | 17.4 | 36
Underground mining Water Requirement t/t |  | 46.7785 | l/s |  |  | Conveyor 4 | 630 | kWE | [6 empty] | 15.8 | 15.8 | 47
TOTAL Water Required |  | 46.7785 | l/s |  |  | Conveyor 5 | 85 | kWE | [6 empty] | 15.7 | 9.1 | 27
[6 empty] | Conveyor 6 | 4300 | kWE | [6 empty] | 15.8 | 13.2 | 15
[6 empty] | Total | 8910 | kWE | [6 empty] | 61.2 | 39.7 | 73
[6 empty] | Potential energy gain |  | kW | [6 empty] | 58 | 58.2 | 30
[6 empty] | Actual Electrical heat gain | 8910 | kWE | [6 empty] | 15.7 | 8.8 | 128
[6 empty] | Belt Length | 4050 | m | [6 empty] | 17.3 | 9.1 | 101
[6 empty] | 10% of Electrical heat | 10% | % | [6 empty] | 15.8 | 23.3 | 21
[6 empty] | Electrical heat | 891 | kWE | [6 empty] | 37.4 | 13.6 | 92
[6 empty] | Linear Heat for electrical equipment | 0.22 | kW/m | [6 empty] | 38 | 13.8 | 62
[15 empty] | 38.2 | 119.4 | 30
[15 empty] | 15.7 | 19.7 | 39
[15 empty] | 15.8 | 20.8 | 95
[15 empty] | 15.7 | 471 | 40
[15 empty] | 19.4 | 23 | 126
[15 empty] | 65.2 | 23 | 55
[15 empty] | 21 | 59 | 49
[15 empty] | 91.5 | 23 | 29
[15 empty] | 98 | 9 | 93
[15 empty] | 11 | 41 | 39
[15 empty] | 16 | 23 | 21
[15 empty] | 25 | 23 | 29
[15 empty] | 21 | 2928.6 | 56
[15 empty] | 293 |  | 47
[15 empty] | 34 |  | 23
[15 empty] | 38 |  | 28
[15 empty] | 5 |  | 40
[15 empty] | 19 |  | 36
[15 empty] | 132 |  | 27
[15 empty] | 35 |  | 23
[15 empty] | 64 |  | 25
[15 empty] | 63 |  | 38
[15 empty] | 31 |  | 46
[15 empty] | 3065.1 |  | 89
21
25
52
107
52
32
26
36
122
26
60
22
64
52
35
42
78
31
29
22
45
84
48
129
22
29
26
40
117
148
27
22
41
31
23
37
58
25
93
44
41
22
26
54
86
27
46
29
39
23
85
27
36
32
109
17
33
20
33
28
28
41
43
48
31
21
21
22
48
7
13
11
5
22
16
20
26
32
25
27
17
43
30
28
44
43
21
19
36
28
43
50
26
40
12
12
26
59
53
13
27
25
9
15
20
8357
Under Development (DO NOT USE - yet)
Note on D58: Usually 11 - 17°CWB
Note on D60: Johan van Sittert: If not known click on BP Link to calculate from collar above sea level
Note on D78: If Value is RED - Delete (Can only use one parameter)

## Planning Graph Calcs 2
Back to INDEX
Graph calcs - Heat Removal capacity of air P956 Env Eng (10°C BAC)
Depth Below Surface in m |  |  | 2500 | m | Enter
Reject Temperature |  |  | 27.5 | °C | Enter
Cooling Capacity of air |  |  | 19.9375 | kJ/Kg
Graph calcs - Heat Removal capacity of air P956 Env Eng (18°C NO BAC)
Depth Below Surface in m |  |  | 2270 | m | Enter
Reject Temperature |  |  | 29 | °C | Enter
Cooling Capacity of air |  |  | 8.448 | kJ/Kg
Expected Wet Bulb Temperature
Total Heat Produced |  |  | 5975 | kW | Enter
Total Refrigeration Available |  |  | 637 | kW | Enter
Available Massflow |  |  | 221.6 | Kg/s | Enter
Depth Below Surface in m |  |  | 2270 | m | Enter
Temp °C |  |  | 27.5111 | °C
|  |  | A | B | C
|  |  | 18 | 10 | 5 | °C | BAC / Surface Temp | Mine Reject Temp | Air cooling capacity
Formulae for A, B and C |  |  | 6.1 | 26 | 38.25 |  | 5 | 29 | 78.1875 | 68.25 | 58.3125 | 48.375 | 38.4375 | 28.5 | 18.5625 | 8.625
[7 empty] | 5 | 28 | 74.1823 | 64.3125 | 54.4427 | 44.5729 | 34.7031 | 24.8333 | 14.9635 | 5.0937
[7 empty] | 5 | 27 | 70.1771 | 60.375 | 50.5729 | 40.7708 | 30.9688 | 21.1667 | 11.3646 | 1.5625
Inputs | Value | Value | Value | Value |  |  | 5 | 26 | 66.1719 | 56.4375 | 46.7031 | 36.9688 | 27.2344 | 17.5 | 7.7656 | -1.9688
Heat | 7116 | 7116 | 7116 | 7116 |  |  | 10 | 29 | 64 | 54.5 | 45 | 35.5 | 26 | 16.5 | 7 | -2.5
Design wb temp | 29 | 29 | 29 | 29 |  |  | 10 | 28 | 59.125 | 49.8333 | 40.5417 | 31.25 | 21.9583 | 12.6667 | 3.375 | -5.9167
Mass flow air | 198 | 198 | 198 | 198 |  |  | 10 | 27 | 54.25 | 45.1667 | 36.0833 | 27 | 17.9167 | 8.8333 | -0.25 | -9.3333
BAC Surf temp (eg 10o) | 5 | 7 | 10 | 18 |  |  | 10 | 26 | 49.375 | 40.5 | 31.625 | 22.75 | 13.875 | 5 | -3.875 | -12.75
Depth below surface | 2500 | 2500 | 2500 | 2500 |  |  | 18 | 29 | 41.3 | 32.5 | 23.7 | 14.9 | 6.1 | -2.7 | -11.5 | -20.3
Output | Value | Value | Value | Value |  |  | 18 | 28 | 35.0333 | 26.6667 | 18.3 | 9.9333 | 1.5667 | -6.8 | -15.1667 | -23.5333
Refrigeration required | 3834.5212 | 3123.9487 | 2058.09 | -784.2 |  |  | 18 | 27 | 28.7667 | 20.8333 | 12.9 | 4.9667 | -2.9667 | -10.9 | -18.8333 | -26.7667
Air Cooling Power KJ/kg | 38.25 | 33.3038 | 26 | 6.1 |  |  | 18 | 26 | 22.5 | 15 | 7.5 | 0 | -7.5 | -15 | -22.5 | -30
Refrigeration required (negative amount means too much refrigeration to achieve reject temp) | -457.5 | 521.8385 | 1968 | 5908.2 |  |  | Depth |  | 500 | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000
Note on D36: M Symons: Use this column for all calculations
Note on B45: M Symons: Balance the Heat with the amount of cooling the air will give together with the amount of refrigeration required to maintain the design reject wetbulb temperature.

## Tons generator
Back to INDEX
Tunnel Square |  |  |  |  | Note: Cost of ORD (Conventional trackbound Development.. 3.5 x 3.0m end Sept 2017 = R53000/m | [9 empty] | 29.2 | tons for every meter |  |  | 2.78 | mean density of Rock [kg/m3]
Where | 3.9 | wD | = | mean density of Rock [kg/m3]
Height | 2.5 | m |  |  | Conv Trackbound mining base price | [7 empty] | 53000
Width | 1.5 | m |  |  | Inflation Rate % | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Length | 1 | m | = | Advance Rate per Day | 4.5% | 38397.1925 | 40206.4843 | 42101.0306 | 44084.8488 | 46162.1454 | 48337.325 | 50615 | 53000 | 55385 | 57877.325 | 60481.8046 | 63203.4858 | 66047.6427 | 69019.7866 | 72125.677 | 75371.3325 | 78763.0424 | 82307.3794 | 86011.2114 | 89881.7159 | 93926.3932
| 23 | Shifts | = | Number of shifts working per month | 5% | 37011.8767 | 38959.8702 | 41010.3897 | 43168.8313 | 45440.875 | 47832.5 | 50350 | 53000 | 55650 | 58432.5 | 61354.125 | 64421.8313 | 67642.9228 | 71025.069 | 74576.3224 | 78305.1385 | 82220.3954 | 86331.4152 | 90647.986 | 95180.3853 | 99939.4045
Area | 3.75 | m² |  |  | 5.5% | 35669.6238 | 37745.6337 | 39942.4695 | 42267.1635 | 44727.1571 | 47330.325 | 50085 | 53000 | 55915 | 58990.325 | 62234.7929 | 65657.7065 | 69268.8803 | 73078.6688 | 77097.9955 | 81338.3853 | 85811.9965 | 90531.6563 | 95510.8974 | 100763.9967 | 106306.0166
Tons Generated | 336.375 | Ton
Production Rate | 0.33637 | kTon/Month |  |  | Cost per ton Mined - Trackbound | 21250.8981 | 22252.2494 | 23300.7847 | 24398.7274 | 25548.4057 | 26752.2572 | 28012.8348 | 29332.8113 | 30652.7878 | 32032.1633 | 33473.6106 | 34979.9231 | 36554.0196 | 38198.9505 | 39917.9033 | 41714.2089 | 43591.3483 | 45552.959 | 47602.8422 | 49744.9701 | 51983.4937 | R/ton
Swel Factor | 1.6 | Times
Meters of rock broken | 1 | m
Volume of broken rock | 6 | m³
[5 empty] | Trackless Rate factor | 2010: 2
[5 empty] | Cost per ton Mined - Trackless | 42501.7963 | 44504.4987 | 46601.5693 | 48797.4548 | 51096.8113 | 53504.5145 | 56025.6696 | 58665.6226 | 61305.5756 | 64064.3265 | 66947.2212 | 69959.8462 | 73108.0393 | 76397.901 | 79835.8066 | 83428.4179 | 87182.6967 | 91105.918 | 95205.6844 | 99489.9402 | 103966.9875 | R/ton
"Raise bore" Round (Tons) | [5 empty] | 2012: $ Cost per m³; 2014: R Cost per m³
Where | 2.4 | wD | = | mean density of Rock [kg/m3] | 1. Crusher chamber m3 – USD110.96 | 2010: Horizontal; 2012: 110.96; 2014: 1448.028
Diameter | 4.5 | m |  |  | 2. Transfer chambers m3 – USD119.03 | 2010: Horizontal; 2012: 119.03; 2014: 1553.3415; 53000 2017: R - USD Exch Rate; 53000 2019: 13.05
| 3.04 | m | = | Advance Rate per Day | As the support classes changes so do the rates. All rates in USD. | 53000 2019: USD/m; 53000 2021: W; 53000 2022: H; 53000 2023: m³; 53000 2024: Type; 53000 2026: $ Cost per m³; 53000 2028: R Cost per m³
| 1 | Shifts | = | Number of shifts working per month |  | 53000 2019: 3530.4525; 53000 2020: 46072.4051; 53000 2021: 5.4; 53000 2022: 6.35; 53000 2023: 34.29; 53000 2024: Decline; 53000 2026: 102.9587; 53000 2028: 1343.6105
Circumference | 14.13 | m |  |  |  | 53000 2019: 3530.4525; 53000 2020: 46072.4051; 53000 2021: 5.4; 53000 2022: 6.35; 53000 2023: 34.29; 53000 2024: Decline; 53000 2026: 102.9587; 53000 2028: 1343.6105
Area | 15.8963 | m² |  |  |  | 53000 2019: 2167.395; 53000 2020: 28284.5048; 53000 2021: 5; 53000 2022: 5; 53000 2023: 25; 53000 2024: Horizontal; 53000 2026: 86.6958; 53000 2028: 1131.3802
Tons Generated | 115.979 | Ton |  |  |  | 53000 2019: 2167.395; 53000 2020: 28284.5048; 53000 2021: 5; 53000 2022: 5; 53000 2023: 25; 53000 2024: Horizontal; 53000 2026: 86.6958; 53000 2028: 1131.3802
Production Rate | 0.11598 | kTon/Month |  |  |  | 53000 2019: 3530.4525; 53000 2020: 46072.4051; 53000 2021: 5.4; 53000 2022: 6.35; 53000 2023: 34.29; 53000 2024: Horizontal; 53000 2026: 102.9587; 53000 2028: 1343.6105
Swell Factor | 1.3 | Times |  |  |  | 53000 2019: 2167.395; 53000 2020: 28284.5048; 53000 2021: 5; 53000 2022: 5; 53000 2023: 25; 53000 2024: Horizontal; 53000 2026: 86.6958; 53000 2028: 1131.3802
Meters of reamed rock | 1 | m
Volume of chips rock | 17.784 | m³
Raise bore Hole / Tunnel (Holing date) Prediction Calculator
[5 empty] | Length of hole / tunnel | 2010: 513.66; 2011: m
Panel Rectangular (Tons) |  |  |  |  | Planned Meters per day | 2010: 6.08; 2011: m
Where | 2.45 | wD | = | mean density of Rock [kg/m3] | Planned Completion date | 2010: 2021-12-11 11:36
Length of Panel | 6 | m |  |  | Date Started | 2010: 2021-09-18
Stoping Width | 2 | m |  |  | Meters achieved | 2010: 285.76; 2011: m
| 4.5 | m | = | Advance Rate per Day | Progress date | 2010: 2021-12-13
| 1 | Shifts | = | Number of shifts working per month | Days since start | 2010: 86; 2011: days
Area | 27 | m²/Day | 27 | m²/Month | Average meters acheved per day to date | 2010: 3.3228; 2011: m
Tons Generated | 132.3 | Ton |  |  | Meters to be Completed | 2010: 227.9; 2011: m
Production Rate | 0.1323 | kTon/Month |  |  | Months to Completion | 2010: 3; 2011: Mths
[5 empty] | Calculated Expected Completion date | 2010: 2022-02-19 14:05
[5 empty] | Variance Planned v.s. Expected | 2010: 70.1034; 2011: Days
[5 empty] | Planned R&R and Off days (per Month) | 2010: 4; 2011: days
[5 empty] | Planned R&R and Off days (Based on months remaining) | 2010: 12; 2011: days
[5 empty] | Planned Public Holiday and Break days | 2010: 4; 2011: days
[5 empty] | Planned / Actual Standing time (i.e. Sub station testing, Safety day training, Main fan outage, Cutter head / motor swop etc.) | 2011: days
Rock produced | 32 | kt/day |  |  | Total expected off days | 2010: 16
Rock produced | 32000 | t.day |  |  | Calculated Est. Completion date, ALL considered | 2010: 2022-03-07 14:05
Hours | 16 | hours
Specific Heat of rock | 0.825 | kJ/kg.
Rock produced (kg/s) | 555.5556 | kg/s
VRT | 59 | °C
Heat from Rock | 27.5 | °C
Reject Temp | 31.5 | °C
Heat from Rock (kW) | 12604.1667 | kW
Kilo Tons per day Calculator
Production Rate Mtpa | 2.4 | Mtpa
Production Rate ktpmth | 200 | ktpmth
Number of shifts per month | 23 | days
Production Rate ktpday | 8.6957 | ktpday
Tunnel Square ~ Development meters from tons
Where | 2.45 | wD | = | mean density of Rock [kg/m3]
Height | 2 | m
Width | 6 | m
| 4.5 | m | = | Advance Rate per Day
Number of shifts working per month | 132 | Shifts | = | Number of shifts working per month
TOTAL Production Rate | 5400 | kTon/day
Number of ends | 8 | each
Daily Production Rate | 675 | kTon/end
Volume of rock | 275.5102 | m³/end
Area | 12 | m²
Meters per day | 22.9592 | m
Number of Shifts | 3 | /day
Number of rounds per shift | 2 | /shift
m/shift | 3.8265
Shifts per month | 22
Tons Generated (Check) | 4950 | Tons
Production Rate | 84.1837 | meters/Month
Development meters from k/tons/day
Production Rate | 5400 | kTon/day
Where | 2.45 | wD | = | mean density of Rock [kg/m3]
Height | 2 | m
Width | 6 | m
Daily Volume | 2204.0816 | m³/day
Area | 12 | m²
Total Meters per day | 183.6735 | m/day
Number of sections | 8 | ea
meteters / section /day | 22.9592 | m
Shifts per month | 22 | Shifts
meters per month per section | 505.102 | m
Ends per section | 3 | ea
meters per month per end | 168.3673 | m
Number of Shifts | 3 | /day
Number of rounds per shift | 2 | /shift
m/shift | 3.5077 | m/round
Check | 5400 | kTon/day
Tons / day | 5400
Density | 2.45
Volume per day | 2204.0816
Area per end | 12
Total dev Meters / day | 183.6735
total dev sections | 8
ends per section | 3
Total dev ends | 24
meteters / section /day | 22.9592
shifts per month | 22
meters per month total per section | 505.102
meters per month total per end | 168.3673 | m
Note on C12: Johan van Sittert: Usually 1.5 to 1.8 for broken rock
Note on K18: As at Sept 2017
Note on M18: As at Sept 2017
Note on R20: As at Sept 2017
Note on R21: As at Sept 2017
Note on C27: Johan van Sittert: Usually 1.2 to 1.5 for reamed rock chips

## Refuge Bays
Back to INDEX
[5 empty] | Component |  | Sequence | Distance(m) x Ve(l/m) = Vt(l)
Specific stope parameters | ENTER Distances | [6 empty] | Acumulative Distance (m) | Ve * Factor | Litre of O2 Consumed
Stope panel length | 30 | m |  |  | Panel |  | 1 | 30 | 4.6 | 138 | [8 empty] | 1138.6 | Rescue pack design / tested Liters air
Strike gully length | 90 | m |  |  | Strike gully |  | 2 | 90 | 2.4 | 216 | [8 empty] | Factor | Distance m
Centre gully length | 220 | m |  |  | Centre gully |  | 3 | 220 | 2.4 | 528
Travelling way inclined | 5 | m |  |  | Trav. Way ° |  | 4 | 5 | 0.9 | 4.5 | [8 empty] | 4.6 | 247.5217 | Gold Mine panel / Face - Crawling UP
Horizontal (Cross cut Travelling) | 150 | m |  |  | Horizontal |  |  | 150 | 0.6 | 90
[5 empty] | Total Distance travelled |  |  | 495m | Total litre O2 consumed | 976.4 | Litre | [7 empty] | 2.7 | 421.7037 | Gold Mine panel / Face - Crawling DOWN
Refuge Pack litre Capacity | 1138.6 | l | [5 empty] | 495
[10 empty] | Refer to table | [8 empty] | 1.4 | 813.2857 | Colery Face (Low Seam) Crawling Horizontal
Note: a typical SCSR provide between 35-50 L/min | 42.5 | 1275 | L |  | Horizontal distance
Test Report Results Calcs | Duration Minutes | Ventilation Rate L/min | Refuge Pack litre Capacity |  | Residual capacity (Vr) of Self rescuer | [13 empty] | 1.6 | 711.625 | Walking semi Upright Horizontal
Rescue Pack 1 | 32.41 | 35 | 1134.35 |  | Vr = |  | 252.1 | litre | (at exit from travelling way) | [9 empty] | 1.2 | 948.8333 | Walking Upright UP +10°
Rescue Pack 2 | 33.15 | 35 | 1160.25 | [15 empty] | 2.4 | 474.4167 | Walking Upright UP +20°
Rescue Pack 3 | 32.34 | 35 | 1131.9 |  | Remaining distance that can be covered | [13 empty] | 2.7 | 421.7037 | Walking Upright UP +30° Ladder
Rescue Pack 4 | 32.23 | 35 | 1128.05 | [15 empty] | 5.4 | 210.8519 | Walking Upright UP +30° No Ladder
Rescue Pack 5 | 31.44 | 35 | 1100.4 |  | dr = |  | 420.1667 | m | [10 empty] | 0.9 | 1265.1111 | Walking Upright DOWN
Rescue Pack 6 | 31.29 | 35 | 1095.15 | [15 empty] | 0.6 | 1897.6667 | Walking Upright HORIZONTAL
Rescue Pack 7 |  |  |  |  | Total distance that can be safely covered (From Panel / workplace to Refuge Bay)
Average |  |  | 1138.6375 | L
[5 empty] | dt = |  | 915.1667 | m
[5 empty] | The refuge bay should be sited at a distance not exceeding | [5 empty] | 420.1667 | m
[5 empty] | from where men may be working (Note O2 consumed not to exceed Refuge Pack litre Capacity See "K10") | [7 empty] | (Kielblock, A.J. and van Rensburg, J.P. [1987] Self-contained rescuer performance as a function of human mechanical efficiency and of escape route terrain, Proc. Symposium on Safety in Coal Mining, paper 8.2, CSIR Conference Publication S420, Pretoria.)
Refuge bay Requirement Calculator
Length of R/Bay | 1 | m
Height of R/Bay | 1 | m |  | Note a 152mm Pipe can carry 2000CFM free air delivery (FAD)
Width of R/Bay | 1 | m |  | 285.7143 | CFM
Volume of R/Bay | 1 | m³
Airchanges Required. | 3 | No/hr
Qty of air required based on Airchange | 0.00083333 | m³/s
Number of bays Compressor can Supply based on Airchange | 647.8894 | bays
Compressor air Supply CFM | 286 | CFM
Compressor air system leakage | 20%
Compressor air Supply CFM | 228.8 | CFM
CFM to m³/s Ratio | 0.00047195 | m³/s | 1 cubic foot per minute = 0.000471947443 cubic meters / second
Compressor air Supply m³/s | 0.10798 | m³/s
pc = compressed pressure | 500 | kPa | Boyle's Law P1 x V1 = P2 x V2 Convert compressed air to free air
Vc = volume of the gas at compressed pressure (cubic feet, cubic meter) | 0.10798 | m³/s
pa = atmospheric pressure (Eg. : 14.7 psia, 101.325 kPa) | 100 | kPa
Va = volume of the gas at atmospheric pressure (cubic ft, cubic m) | 0.53991 | m³/s
Person air usage l/min | 85 | l/min
Volume per person | 0.0014167 | m³/s |  | 1 l / minute = 1.66666667 × 10-5 cubic meters / second | [5 empty] | 1.6667e-05 |  | m³/s
Volume required in Bay | 0.0023611 | m³/s
Area of R/Bay | 1 | m²
Area allocated per person | 0.6 | m²
People in R/Bay | 1.6667 | Persons |  |  |  |  | 0.0014167 | m³/s per person
Number of bays Compressor can Supply based on Req. per person | 228.6669 | bays |  |  |  |  | 1.4167 | m³/s
Number of People Compressor can Supply based on Req. per person | 381.1114 | People |  |  |  |  | 85 | m³/minute
Refuge Bay Breathable Air Systems
(See MVS Journal Volume 54, 2 April/June 2001)
Calculating the required compressed air supply for a refuge bay
1. Recommended compressed air supply per person (for oxygen uptake of 0.5 l/min & CO2 dilution) | = | 85 | l/min
| = | 1.4167 | l/s
| = | 0.0014167 | m3/s
| L | x | W | Refuge Bay Area
2. Refuge bay size (example) | 27.5 | x | 3 | 82.5 | m2
3. Area allocated per person | = | 0.6 | m2
4. Number of persons allowed in refuge bay at 0.6m2 per person | = | 137.5 | Pers |  | Single formula
5. Airflow rate required for refuge bay | = | 0.19479 | m3/s |  | 0.38958
Refuge bay capacity vs people calc
Steady State Year (Future Planning) | Area 1 | Area 2
Refuge bays on Dip [every third strike approx 300m] | 5 | 3
Number of refuge bays | [12 empty] | At 30m/s
Sub Total | 5 | 3 | [6 empty] | Bay | BP |  | Personel Capacity - Bay Size | Personel Capacity - Air Supply | Installed Pipe Size
Total | 8 | [7 empty] | Refuge Bay 1 | 112.2 |  | 194 | 185 | 50mm
Total air required, FAD [free air delivery] | 1.5583 | m3/s | [6 empty] | Refuge Bay 2 | 112.2 |  | 157 | 185 | 50mm
Leakage [pipes, fittings, valves etc] 20% | 1.87 | m3/s | [6 empty] | Refuge Bay 3 | 112.3 |  | 30 | 185 | 50mm
[9 empty] | Refuge Bay 4 | 113 |  | 19 | 45 | 25mm
Max number of people underground [Day shift / Max amount of people] | 1000 | [7 empty] | Refuge Bay 5 | 112.5 |  | 233 | 184 | 50mm
Air required for people UG | 1.4167 | m3/s | [6 empty] | Refuge Bay 6 | 113.5 |  | 293 | 183 | 50mm
Air available from compressors ("Free Air") | 6.1 | m3/s | [6 empty] | Refuge Bay 7 | 115 |  | 273 | 180 | 50mm
Plan for 8 refuge bays with 137,5 people | 1100 |  | Personnel | [5 empty] | Refuge Bay 8 | 116 |  | 253 | 179 | 50mm
Refuge bay capacity exceeds number of people | 1.1 | times | [6 empty] | Refuge Bay 9 | 116.9 |  | 220 | 177 | 50mm
[9 empty] | Refuge Bay 10 | 117 |  | 130 | 177 | 50mm
Refuge bay comp air pipe flow calc | [8 empty] | Refuge Bay 11 | 117 |  | 130 | 177 | 50mm
Number of persons in refuge bay at 0.6m2 per person | = | 100 | Pers |  |  | 0.7735 |  |  |  | TOTAL |  | 1532 | 1257
Refuge Bay Compressed air feed PRESSURE |  | 99.9 | kPa |  |  | 2784.6 |  |  | Note a 150mm pipe can sustain 1550 People without any air whistles and leakage
Atmospheric pressure at Bay |  | 96.9 | kPa | [5 empty] | Note Bay 1-5 will get 80mm pipes tapped from the 150mm pipe
Airflow rate required for refuge bay | = | 0.14167 | m3/s | 510 | m³/Hr | 0.00014167 | l/min |  | Air whistle consumption--- 6.35mm Diameter @ 40m/s = 0.0013m³/s
Compressed air Pipe supplying Refuge Bay | = | 50 | mm | 181.186 |  |  | 7.75 |  | Permanent prohibition to be placed on any compressed air being tapped from the refuge bay compressed air feed line
Pipe size in Meters | = | 0.05 | m
Max Velocity in Compressed air pipe | = | 30 | m/s
Pipe size in Square Meters | = | 0.0019635 | m² | Single formulae
Max Compressed air Quantity that can be supplied with Compressed air pipe | = | 0.058905 | m³/s | 0.019615 |  |  | Single formula (m³/s)
Max "FREE AIR" Quantity that can be supplied with Compressed air pipe | = | 0.060729 | m³/s | 218.6228 | m³/Hr |  | 0.10121
|  | 0 |  | Air whistle qty 0.01 x 10
Velocity Table
Air Ducts | Air Velocity
| (m/s) | (ft/min)
Combustion air duct | 12 - 20 | 2400 - 4000
Air inlet to boiler room | 1 - 3 | 200 - 600
Warm air for house heating | 0.8 - 1.0 | 150 - 200
Vacuum cleaning pipe | 8- 15 | 1500 - 3000
Compressed air pipe | 20 - 30 | 4000 - 6000 | NOTE: This can be as high as 50m/s
Ventilation ducts in hospitals | 5 - 8 | 1000 - 1500
Ventilation ducts in office buildings | 7 - 11 | 1200 - 2000
Example - Converting a Compressed Air Volume to a Free Air Volume | People | 1 | 100 | 500 | 1000 | 1500
A compressed air volume flow of 10 acfm at 100 psig must be multiplied with a compression ratio approx. 8 to find the free air flow at atmospheric pressure. | Airflow Volume Req | 0.00142 | 0.142 | 0.7083 | 1.4167 | 2.125
•in this case approx. 80 scfm | m³/s Free Air @ 103.2kPa (400kPa) | 0.0054852 | 0.55178 | 2.7491 | 5.4908 | 8.2357
| m³/hr Free Air @ 103.2kPa (400kPa) | 19.7 | 1986.4209 | 9896.7566 | 19766.7315 | 29648.6276
Calculate the hole size diameter for Refuge Bay Chamber valve to achieve pre-set air change
Refuge Bay Chamber Length (m) | = | 15 | m
Refuge Bay Chamber Width (m) |  | 6 | m
Refuge Bay Chamber Height (m) |  | 5.5 | m
Refuge Bay Chamber Cubic Dimension (Total Volume m³) |  | 495 | m³
Refuge Bay Chamber Airchange required |  | 0.5 | No of / hr
Refuge Bay Compressed air feed PRESSURE |  | 600 | kPa | ▲ Pressure
Atmospheric pressure at Bay |  | 116.7 | kPa | 483,3 kPa
Airflow rate required for refuge bay | = | 0.06875 | m3/s
Compressed air Pipe supplying Refuge Bay / Hole size in valve | = | 19 | mm
Pipe size in Meters | = | 0.019 | m | 0.043325
Max Velocity in Compressed air pipe | = | 50 | m/s
Pipe size in Square Meters | = | 0.00028353 | m²
Max Compressed air Quantity that can be supplied with Compressed air pipe | = | 0.014176 | m³/s | [7 empty] | 0.40317 | 0.79375 | 1.5875 | 3.175 | 6.35 | 9.525 | mm
Max "FREE AIR" Quantity that can be supplied with Compressed air pipe | = | 0.072887 | m³/s | [6 empty] | 0.00047195
[10 empty] | Area m² | 1.2767e-07 | 4.9483e-07 | 1.9793e-06 | 7.9173e-06 | 3.1669e-05 | 7.1256e-05
[10 empty] | Diameter m | 0.00040317 | 0.00079375 | 0.0015875 | 0.003175 | 0.00635 | 0.009525 | m
Calculate the heat load of people | [8 empty] | kPa | 482.6 | 8.0556e-05 | 0.00032222 | 0.0012944 | 0.0051722 | 0.020667 | 0.046611 | m³/s
[10 empty] | 551.6 | 8.8889e-05 | 0.00035 | 0.0014556 | 0.0057667 | 0.023083 | 0.05075
Heat Loat of a resting person |  | 100 | watt per Person * | [6 empty] | 620.5 | 0.0001 | 0.00040556 | 0.0015889 | 0.0064167 | 0.025556 | 0.057389
Heat Loat of a resting person in kW |  | 0.1 | kW per Person | [6 empty] | 689.5 | 0.00011111 | 0.00043056 | 0.0017528 | 0.0070056 | 0.028028 | 0.063056
Number of persons in refuge bay at 0.6m2 per person |  | 180 | Pers | [6 empty] | 861.8 | 0.00013333 | 0.00053889 | 0.0021278 | 0.0085139 | 0.033944 | 0.076528
Refuge Bay Heat Load |  | 18 | kW | [6 empty] | Velocity Calc
BTU |  | 61418.5494 | [8 empty] | 63.0985 | 65.1176 | 65.3982 | 65.3281 | 65.2579 | 65.4138 | 64.9357 | m/s
* Note: typically a resting person will emit 70 - 100W of heat | [10 empty] | 69.626 | 70.7311 | 73.5379 | 72.8362 | 72.8889 | 71.2223 | 71.8071 | m/s
A working person will emit 180 - 200W of heat | [10 empty] | 78.3292 | 81.9583 | 80.2742 | 81.0461 | 80.6953 | 80.5393 | 80.4737
A hard working person will emit 200 - 240W of heat | [10 empty] | 87.0325 | 87.0105 | 88.5543 | 88.4841 | 88.5016 | 88.4919 | 88.0125
[11 empty] | 104.439 | 108.9035 | 107.5001 | 107.5352 | 107.1843 | 107.3988 | 107.1601
Calculate the Qty of air in a pipe | [10 empty] | 82.4778 | [5 empty] | m/s
ATKINSON’S FORMULA - Qty Calc |  | (Qty)
V = | P. A x 1.2
| KCL w | [9 empty] | 0.29 | 1.16 | 4.66 | 18.62 | 74.4 | 167.8
Pipe Diameter = | 50 | mm | Enter | [7 empty] | 0.32 | 1.26 | 5.24 | 20.76 | 83.1 | 182.7
Pipe Diameter = | 0.05 | m | [8 empty] | 0.36 | 1.46 | 5.72 | 23.1 | 92 | 206.6
L = (in meters) | 50 | m | Enter | [7 empty] | 0.4 | 1.55 | 6.31 | 25.22 | 100.9 | 227
Refuge Bay Compressed air feed PRESSURE | 500 | kPa | [8 empty] | 0.48 | 1.94 | 7.66 | 30.65 | 122.2 | 275.5
Atmospheric pressure at Bay | 111.75 | kPa
P Drop = | 388250 | Pa | Enter | [5 empty] | Factor 0.97 Well Round Oriface |  | 61.2056 | 63.164 | 63.4363 | 63.3682 | 63.3002 | 63.4514
w = air density | 1.125 | Kg/m³ | Enter | 1.2 | Kg/m³ |  |  |  | Factor 0.61 Sharp Oriface |  | 38.4901 | 39.7217 | 39.8929 | 39.8501 | 39.8073 | 39.9024
K = | 0.0025 | ns²/m⁴ | Enter | [5 empty] | AVERAGE |  | 49.8478 | 51.4429 | 51.6646 | 51.6092 | 51.5537 | 51.6769 | m/s
C = | 0.15708 | m | [8 empty] | 51.2992 | [5 empty] | m/s
A = | 0.0019635 | m² | Theoretical Velocity
Velocity inside pipe | 50 | m/s | 203.5027 | m/s
Qty (m³/s) | 0.098175 | m³/s
Qty (m³/s) - Free Air | 0.43926 | m³/s
Can Sustain XX Persons | 310.0664 | People
Water tank Calculator (When using a pipe as a water Tank)
Water tank Calculator (When using a pipe as a water Tank)
Length of Pipe | 8 | m
Diameter of Pipe in mm | 300 | mm
Volume of water required per person for 24Hrs | 2 | Litre per person
Refuge bay People Capacity | 128 | persons
Diameter of Pipe in meters | 0.3 | m
Area of Pipe | 0.070686 | m²
Volume of Pipe | 0.56549 | m³
Volume of Pipe | 565.4867 | Litre Water |  | 2827.4334
Water required in a 24 Hr Period | 256 | Litre |  | 1413.7167
Days Tank will sustain Refuge Bay | 2.2089 | Days |  | 2.0196
Water Container Calculator (When using Water Containers)
Volume of water per containers | 20 | Litre Water
Volume of water required per person for 24Hrs | 2 | Litre per person
Refuge bay People Capacity | 165 | Persons
Water required in a 24 Hr Period | 330 | Litre
Number of Containers required to sustain Refuge Bay for 24 hrs | 17 | Containers per day
To ensure the CO2 content levels out below the TLV-TWA of 0.5%, a fresh air supply of 85 litres per minute per person is required
(See MVS Journal Volume 54, 2 April/June 2001 page 4)
Compressed Air
It has been previously shown that an oxygen uptake of 0.5 litres/minute is a good design figure for entrapment. To ensure the CO2 content levels out below the TLV-TWA of 0.5%, a fresh air supply of 85 litres per minute per person is required. This flow rate will result in a “steady state” oxygen content of
about 20.3%. Lower supplies of fresh air are sometimes quoted (e.g. 2.5 cfm per person which is about 70 litres/minute); however, these are based on unstressed, resting breathing rates (7.5 litres/minute) with an equivalent oxygen uptake (0.3 litres/minute) and do not allow for any additional persons (above the design figure) inside the ERS.
Note on C5: Typicaly - ±30-35m
Note on C6: Typicaly - ±90m (Max)
Note on C7: Typicaly - ±180-250m
Note on C8: Typicaly - ±30-60m
Note on C9: Typicaly - ±150-250m (XC Length)
Note on C11: Get this form manufacturer or latest Rescue pack test report - See tabulation of results below: "Test Report Results Calcs"
Note on C47: To ensure the CO2 content levels out below the TLV-TWA of 0.5%, a fresh air supply of 85 litres per minute per person is required (See MVS Journal Volume 54, 2 April/June 2001 page 4) Compressed Air It has been previously shown that an oxygen uptake of 0.5 litres/minute is a good design figure for entrapment. To ensure the CO2 content levels out below the TLV-TWA of 0.5%, a fresh air supply of 85 litres per minute per person is required. This flow rate will result in a “steady state” oxygen content of about 20.3%. Lower supplies of fresh air are sometimes quoted (e.g. 2.5 cfm per person which is about 70 litres/minute); however, these are based on unstressed, resting breathing rates (75 litres/minute) with an equivalent oxygen uptake (0.3 litres/minute) and do not allow for any additional persons (above the design figure) inside the ERS.
Note on B58: by Ralph Mcintyre
Note on D61: To ensure the CO2 content levels out below the TLV-TWA of 0.5%, a fresh air supply of 85 litres per minute per person is required (See MVS Journal Volume 54, 2 April/June 2001 page 4) Compressed Air It has been previously shown that an oxygen uptake of 0.5 litres/minute is a good design figure for entrapment. To ensure the CO2 content levels out below the TLV-TWA of 0.5%, a fresh air supply of 85 litres per minute per person is required. This flow rate will result in a “steady state” oxygen content of about 20.3%. Lower supplies of fresh air are sometimes quoted (e.g. 2.5 cfm per person which is about 70 litres/minute); however, these are based on unstressed, resting breathing rates (7.5 litres/minute) with an equivalent oxygen uptake (0.3 litres/minute) and do not allow for any additional persons (above the design figure) inside the ERS.
Note on D92: Johan van Sittert: See Velocity Table Below NOTE: This can be as high as 50m/s
Note on D125: Johan van Sittert: See Velocity Table Below NOTE: This can be as high as 50m/s See Table L to Q Line -152 Below Thus,as a guide: ▲P = 300kPa - Use 30m/s ▲P = 400kPa - Use 40m/s ▲P = 500kPa - Use 50m/s
Note on C157: Max Vel in pipe
Note on D166: Johan van Sittert: Litre (international spelling) or liter (American spelling)

## Gas
[6 empty] | Back to INDEX | [5 empty] | Practical Certificate
Gas Table
| GAS DILUTION | [10 empty] | CHARACTERISTICS OF SOME GASES FOUND AT MINING OPERATIONS
[12 empty] | GAS | CHEMICAL | SOURCES OF GAS | METHODS OF DETECTION | DANGERS | SENSES | EXPLOSIVE | SPECIFIC GRAVITY | OEL
|  |  | Q | = | Q1 x 10⁶ | =-Q1 | [6 empty] | FORMULA
[5 empty] | MAC - N | [6 empty] | Carbon Dioxide | CO2 | Blasting Oxidation of timber & fuels. Fires & diesels | Detector tubes, electronic instruments, and chemical analysis | Oxygen deficiency - Asphyxia | Colourless and odourless | No | 1,53 | General air
[19 empty] | Heavier than air | 5000 ppm or 0.5%
| Where | 0.3953 | Q1 | = | volume or mass flow rate of gas emission [m3/s or kg/s] | [6 empty] | Carbon Monoxide | CO | Incomplete combustion, Fires, Blasting and Diesel equipment | Detector tubes, electronic instruments | Poisonous and Explosive | Colourless and odourless | Yes | 0,97 | General air
|  | 1000 | MAC | = | maximum allowable gas concentration [after mixing] in parts Per million by volume or mass | [12 empty] | 12,5% - 74,2% | Similar to air | 30 ppm or 0.003%
|  | 0 | N | = | gas concentration in normal air in parts per million by volume or mass | [6 empty] | Oxides of Nitrogen (Nitrous fumes) | NOx – mainly NO and NO2 | Explosives and diesel equipment | Detector tubes, electronic instruments | Oedema – blistering of lungs, lungs become waterlogged | Reddish-brown | No | 1,6 | General air
| Q | 395.3 | m³/s or kg/s | [13 empty] | Can smell and acid taste on tongue |  | Heavier than air | 3 ppm or 0.0003%
[12 empty] | Hydrogen | H2 | Battery charging and Can occur with methane. | Detector tubes, Flammable Gas Measuring Instrument and laboratory analysis | Highly explosive | Nil | Yes | 0,07 | Nil (<1,4%)
[18 empty] | 4.0% - 74.0% | Lighter than air
[12 empty] | Hydrogen Sulphide | H2S | Acid water on pyrites and stagnant water. | Detector tubes, electronic instruments | Poisonous. | Smell of rotten eggs | Yes | 1,2 | General air
| GAS MIXING | [7 empty] | i.e. |  |  |  |  | Can occur in conjunction with methane. |  | Explosive |  | 4,0% - 44,0% | Heavier than air | 10 ppm or
[10 empty] | 1000 | 1m³ Air Volume | [8 empty] | 0.001%
|  | Percentage gas % |  | = | Total Qty Gas | x 100 |  |  |  | 1800 | sec/30min | Methane | CH4 | Decay of vegetable and organic matter. Faults, fissures, dykes | Detector tubes, Flammable gas measuring instrument. | Burns, explodes and oxygen deficiency | Nil – impurities may smell | Yes | 0,55 | <1.4%
[5 empty] | Total Qty Air + Qty Gas |  |  |  |  | 7117 | ppm | [6 empty] | 5,0% - 15,0% | Lighter than air
[10 empty] | 0.7117 | % | Oxygen | O2 | A main constituent of air | Deficiencies by detector tubes, electronic instruments | Deficiency - below 17% can be fatal | Nil | No | 1,10 | Not less than: >19.0%
| Where | 0.003954 | m³/s | = | Total quantity gas = m³/s |  |  |  |  | 0.00039539 | %/s
|  | 40 | m³/s | = | Total quantity air + quantity gas = m³/s |  |  |  |  | 0.0014234 | m³/s | Ammonia | NH3 | Blasting. Excessive liming of settlers. Refrigerants | Detector tubes, electronic instruments Smell (Extremely pungent odor is detectable from 5ppm and becomes iritating at 25ppm | Arrested breathing results in oedema | Colourless. | No | 0,6 | 25 ppm
|  | 0.009884 | % | = | % Gas | [10 empty] | (flooding of the lungs) | Can smell (extremely pungent) and irritation of eyes, nose and throat | LEL15,0% - UEL28,0% Autoignition temperature - 651 °C Ammonia does not burn readily or sustain combustion, except under narrow fuel-to-air mixtures of 15–25% air. | Lighter than air
|  | 98.8402 | ppm | = | parts-per million (ppm) |  | 120000 | ppm | = | parts-per million (ppm) |  | Chlorine | Cl2 | Water purification plants | Detector tubes, electronic instruments, smell | Poisonous & causes intense irritation of eyes, nose & throat | Smell greenish – yellow colour | No | 2,5 | 0.5 ppm
[7 empty] | 12 | % | = | % Gas | [8 empty] | Heavier than air
[12 empty] | Sulphur Dioxide | S02 | Smelting operations, Sulphuric acid plants, combustion of pyrite, diesel exhaust | Detector tubes, electronic instruments, smell | Poisonous, burns eyes, nose, throat & lungs | Smell | No | 2,22 | 2 ppm
Combustables (LEL and UEL) | [6 empty] | 12 | % | = | % Gas | [8 empty] | Heavier than air
[7 empty] | 120000 | ppm | = | parts-per million (ppm) |  | Sulphuric Acid Mist | H2SO4 | Chemical processes using sulphuric acid | Detector tubes, chemical analysis | Poisonous. Irritates eyes, nose, throat & skin | Nil | - | - | 1 mg/m3
[12 empty] | Acetylene | C2H2 | Acetylene Bottles or appears as a side product in the ethylene stream from cracking of hydrocarbons | Smell, Detector tubes, electronic instruments | Explosive | Odourless - Smell of garlic-like (Added for safety) | LEL 2.5% Yes - Autoignition temperature 300 °C | 1.097 g/L = 1.097 kg/m | REL 2500 ppm
Heavier than air
[12 empty] | LPG (Liquefied Petroleum Gas) | Mixture of: Propane (C3H8) and Butane (C4H10) | LPG Bottles (LPG is prepared by refining petroleum or "wet" natural gas, and is almost entirely derived from fossil fuel sources) | Smell, Detector tubes, electronic instruments | Explosive | Odourless - Odor of rotten cabbages (Added for safety) | Yes | 0.5–0.58 kg/L | 1000 ppm (1800 mg/m3) over an 8-hour workday
[18 empty] | LEL 1.9-2.1% (2000ppm) | Lighter than air
[12 empty] | Oxygen (dioxygen) | O8 - (Oxygen is a chemical element with symbol O and atomic number 8) O2. Diatomic oxygen gas constitutes 20.8% of the Earth's atmosphere. | Normal atmosphere and Oxygen Bottles | Electronic instruments | Normally - None Explosive - Highly concentrated sources of oxygen promote rapid combustion. Fire and explosion hazards exist when concentrated oxidants and fuels are brought into close proximity; an ignition event, such as heat or a spark, is needed to trigger combustion. Oxygen is the oxidant, not the fuel, but nevertheless the source of most of the chemical energy released in combustion. | Odourless | - | Density (at STP) 1.429 g/L | -
when liquid (at b.p.) 1.141 g/cm3
[12 empty] | Lead Fumes | Pb | Assay of Gold Ore & Zinc preparation of cyanide – extracted Gold | Dräger | Poisonous | Nil | No | Heavier than air | 0,15mg/m³
[12 empty] | Mercury Vapour | Hg | Gold smelting | Dräger | Poisonous can be absorbed through the skin | Nil | No | Heavier than air | 0,05mg/m³
[12 empty] | Hydrogen cyanide (Prussic acid gas) | HCN | Cyanide process in gold recovery. Back-filling and Burning plastics | Smell and Dräger | Poisonous. Explosive (5,6 -40%). Can be absorbed through the skin | Smell (bitter almonds) | Yes | 0,94 Lighter than air | 10 ppm
[12 empty] | Arsenic | AsH3 | Arsenic acid in solution used in refining process (Platinum and Gold) | Smell and Dräger | Poisonous | Smell (Garlic) | No | 2,71 Heavier than air | 0,05 p.p.m
Toxins
Note on W22: For Ammonia to be regarded as an explosive gas / fluid you will need to have LEL 150000ppm and UEL 280000ppm ammonia present in the atmosphere, 25ppm OEL limit Ammonia is also very susceptible to humidity, the slightest change in that will cause a disruption in the combustion process (nearly perfect dry air conditions will needed to be created to cause a fire or explosion) The high auto ignition temperature should also be regarded, to get ammonia to ignite - 651°C is required, this is quite high!! Additionally as soon as Ammonia is ignited the combustion process changes the percentage in the atmosphere quite drastically and the combustion process is disrupted – tests done had only single digit increases in temperatures observed. So in short to get all systems perfectly aligned to get a fire and or explosion is nearly impossible.
Note on X22: Note: 0.86 kg/m3 (1.013 bar at boiling point) 0.769 kg/m3 (STP)[1] 0.73 kg/m3 (1.013 bar at 15 °C) 681.9 kg/m3 at −33.3 °C (liquid)[2] 817 kg/m3 at −80 °C (transparent solid)[3]
Note on Y30: Recommended Exposure Limit (REL)
Note on Y32: LPG is considered immediately dangerous to life and health (due solely to safety considerations pertaining to risk of explosion)

## Air Flow
Back to INDEX
Natural Ventilation Pressure [NVP] | [5 empty] | Fraction of Area Open Calculator |  |  |  |  | SP and VP Calculator
a. Density Formula Method [when there are no fans in the circuit] | [11 empty] | Qty | 326.8
|  | NVP | = | [wD - wU] x H x 9.79 |  | Where - Pipes | 0.76 | m | = | Pipe diameter size |  | Area= m² | 7.069
[7 empty] | 5 | No | = | Number of OPEN Pipes |  | Density ρ kg/m³ | 1.045
Where | 1.175 | wD | = | mean density of downcast air [kg/m3] |  |  | 0.45365 | m² | = | Regulator pipe Area |  | V | 46.23
| 1.135 | wU | = | mean density of upcast air [kg/m3] |  |  | 2.2682 | m² | = | Combined Open Regulator pipe Area |  | Vp | 1116.6946
| 923 | H | = | vertical distance from the top to the bottom of the circuit [m] |  | Where - Tunnel | 3.2 |  | = | Tunnel Width |  | Total Press Pa | 1740
| 9.79 |  | = | constant for gravitational acceleration [m/s2] |  |  | 3.2 |  | = | Tunnel Height |  | Static Press Pa | 623.3054
NVP = | 361.4468 | Pa |  |  |  |  | 10.24 | m² | = | Tunnel Area
[6 empty] | Regulator % Open | 22.1507 | %
Natural Ventilation Pressure [NVP] | [5 empty] | Fraction of Area Open Calculator
b. P-V Diagram Method [with or without fans in the circuit] and
|  | NVE | = | Pv |  | Where - Regulator | 0.14 | m | = | Regulator OPEN Width
|  | NVP | = |  |  |  | 5 | m | = | Regulator OPEN Height
[7 empty] | 0.7 | m² | = | Regulator Open Area
Where | 99.372 | NVE | = | natural ventilation energy [kJ/kg] |  | Where - Tunnel | 5 |  | = | Tunnel Width
| 101.4 | P | = | barometric pressure [kPa] |  |  | 5 |  | = | Tunnel Height
| 0.98 | v | = | specific volume [m3/kg] |  |  | 25 | m² | = | Tunnel Area
NVP = | 101.4 | Pa
[6 empty] | Regulator % Open | 2.8 | %
REYNOLDS NUMBER | [5 empty] | Air viscosity
|  | Re | = |  |  | Value A | 20 | = | 17.9 | Viscosity at 20°C
[6 empty] | Value B | 27.5 | = | 18.2375 | Viscosity at 27,5°C
Where | 1.15 | w | = | density [kg/m3] |  | Value C | 40 | = | 18.8 | Viscosity at 40°C
| 12 | V | = | velocity [m/s]
| 12 | D | = | diameter [m]
| 18.2 |  | = | Viscosity at 27,5°C
| 1.82e-05 | m | = | dynamic viscosity [Ns/m2]
Re | 3016.4385 |  | = | Reynolds number [dimensionless]
- Note number above 3000 is turbulent
CONSERVATION OF ENERGY | [5 empty] | Mentis Grating Calculator
M
u + Pv + |  | + Zg | = | Constant |  | Width of cover | 4500 | mm |  | 4.5
[6 empty] | Length of cover | 4500 | mm |  | 4.5
[6 empty] | Mentis Grating Area | 20250000 |  |  | 20.25
Where |  | u | = | internal energy [J/kg] |  | Mentis Grating X bar spacing | 40 | mm |  | 4e-05
|  | P | = | pressure [Pa] |  | Mentis Grating bearing and X bar size | 6 | mm |  | 6e-06
|  | v | = | specific volume [m3/kg] |  | Number of X Bars | 113
|  | V | = | velocity [m/s] |  | Number of Bearing Bars | 113
|  | Z | = | elevation [m] |  | X Bar total Length | 678 |  |  | 0.678
| 9.79 | g | = | gravitational acceleration [9.79 m/s2] |  | Bearing Bar Length | 678 |  |  | 0.678
Constant | 0 |  |  |  |  | Bearing and X Bar Area | 459684 |  |  | 0.45968
Barometric increase with depth
Where | 97 | kPa | = | Surface BP
| 0.4 | H in km | = | vertical distance from the top to the bottom of the circuit [km]
| 1.085 | Mean Density
| 9.79 |  | = | constant for gravitational acceleration [m/s2]
NVP = | 101.2489 | kPa
Pressure change with Density Change |  |  |  |  | (PRESSURE / DENSITY RELATIONSHIP)
|  | Re | = |  | Air pressure varies directly as an air density change:-
Where | 1917 | P1 | = | pressure [Pa]
| 1.1 | w1 | = | density [kg/m3]
| 1.1 | w2 | = | density [kg/m3]
P2 = | 1917 | Pa
P2 = | 1.917 | kPa
Mixing of Airstreams
Sc =
Where | 13.5 | MA | = | Massflow from air stream A
| 88.6 | SA | = | Sigma heat from air stream A
| 2.7 | MB | = | Massflow from air stream B
| 84.3 | SB | = | Sigma heat from air stream B
| 1196.1 | MA x SA | = | the total kW of heat from air stream A
| 227.61 | MB x SB | = | the total kW of heat from air stream B
Sc | 87.8833 | sigma heat content of the mixture [kJ/kg]
Quantity change with Density Change
Where | 1 | Q1 | = | Qty 1 m³/s
| 1 | w1 | = | density [kg/m3]
| 1.4 | w2 | = | density [kg/m3]
Q2 = | 0.71429 | m³/s

## Long Columns
Back to INDEX
[6 empty] | Diesel kW | Dilution Factor
Pipe Diameter (in meters) | 1.22 | m |  |  |  | 570 | 0.06 |  | 34.2
Leakage Allowed | 10% | /100m |  | Qty Required |  | 34.2 m³/s |  | +50% | Total
Leakage Allowed (Length increment) | 0.05 | /100m |  |  |  |  | 34.2 | 17.1 | 51.3 | Diesel dilution + 50% m³/s
Length increments = (in meters) | 50 | m
Calculated TOTAL Leakage % | 0 | 5 | 9.75 | 14.2625 | 18.5494 | 22.6219 | 26.4908 | 30.1663 | 33.658 | 36.9751 | 40.1263 | 43.12 | 45.964
Length - Total | 10 | 60 | 110 | 160 | 210 | 260 | 310 | 360 | 410 | 460 | 510 | 560 | 610 | 660 | 710 | 760 | 810 | 860 | 910 | 960 | 1010 | 1060 | 1110 | 1160 | 1210 | 1260 | 1310 | 1360 | 1410 | 1460 | 1510 | 1560 | 1610 | 1660 | 1710 | 1760 | 1810 | 1860 | 1910 | 1960 | 2010 | 2060 | 2110 | 2160 | 2210 | 2260 | 2310 | 2360 | 2410 | 2460 | 2510 | 2560 | 2610 | 2660 | 2710 | 2760 | 2810 | 2860 | 2910 | 2960 | 3010 | 3060 | 3110 | 3160 | 3210 | 3260 | 3310 | 3360 | 3410 | 3460 | 3510 | 3560 | 3610 | 3660 | 3710 | 3760 | 3810 | 3860 | 3910 | 3960 | 4010 | 4060 | 4110 | 4160 | 4210 | 4260 | 4310 | 4360 | 4410 | 4460 | 4510 | 4560 | 4610 | 4660 | 4710 | 4760 | 4810 | 4860 | 4910 | 4960 | 5010 | 5060 | 5110 | 5160 | 5210 | 5260 | 5310 | 5360 | 5410 | 5460 | 5510 | 5560 | 5610 | 5660 | 5710 | 5760 | 5810 | 5860 | 5910 | 5960 | 6010 | 6060 | 6110 | 6160 | 6210 | 6260 | 6310 | 6360 | 6410 | 6460 | 6510 | 6560 | 6610 | 6660 | 6710 | 6760 | 6810 | 6860 | 6910 | 6960 | 7010 | 7060 | 7110 | 7160 | 7210 | 7260 | 7310 | 7360 | 7410 | 7460 | 7510 | 7560 | 7610 | 7660 | 7710 | 7760 | 7810 | 7860 | 7910 | 7960 | 8010 | 8060 | 8110 | 8160 | 8210 | 8260 | 8310 | 8360 | 8410 | 8460 | 8510 | 8560 | 8610 | 8660 | 8710 | 8760 | 8810 | 8860 | 8910 | 8960 | 9010 | 9060 | 9110 | 9160 | 9210
Qty (m³/s) | 45 | 42.75 | 40.6125 | 38.5819 | 36.6528 | 34.8201 | 33.0791 | 31.4252 | 29.8539 | 28.3612 | 26.9432 | 25.596 | 24.3162 | 23.1004 | 21.9454 | 20.8481 | 19.8057 | 18.8154 | 17.8746 | 16.9809 | 16.1319 | 15.3253 | 14.559 | 13.8311 | 13.1395 | 12.4825 | 11.8584 | 11.2655 | 10.7022 | 10.1671 | 9.6587 | 9.1758 | 8.717 | 8.2812 | 7.8671 | 7.4738 | 7.1001 | 6.7451 | 6.4078 | 6.0874 | 5.783 | 5.4939 | 5.2192 | 4.9582 | 4.7103 | 4.4748 | 4.2511 | 4.0385 | 3.8366 | 3.6448 | 3.4625 | 3.2894 | 3.1249 | 2.9687 | 2.8202 | 2.6792 | 2.5453 | 2.418 | 2.2971 | 2.1823 | 2.0731 | 1.9695 | 1.871 | 1.7775 | 1.6886 | 1.6042 | 1.5239 | 1.4478 | 1.3754 | 1.3066 | 1.2413 | 1.1792 | 1.1202 | 1.0642 | 1.011 | 0.96047 | 0.91244 | 0.86682 | 0.82348 | 0.78231 | 0.74319 | 0.70603 | 0.67073 | 0.63719 | 0.60533 | 0.57507 | 0.54631 | 0.519 | 0.49305 | 0.4684 | 0.44498 | 0.42273 | 0.40159 | 0.38151 | 0.36244 | 0.34431 | 0.3271 | 0.31074 | 0.29521 | 0.28045 | 0.26642 | 0.2531 | 0.24045 | 0.22843 | 0.217 | 0.20615 | 0.19585 | 0.18605 | 0.17675 | 0.16791 | 0.15952 | 0.15154 | 0.14396 | 0.13677 | 0.12993 | 0.12343 | 0.11726 | 0.1114 | 0.10583 | 0.10054 | 0.095509 | 0.090734 | 0.086197 | 0.081887 | 0.077793 | 0.073903 | 0.070208 | 0.066698 | 0.063363 | 0.060195 | 0.057185 | 0.054326 | 0.051609 | 0.049029 | 0.046577 | 0.044249 | 0.042036 | 0.039934 | 0.037938 | 0.036041 | 0.034239 | 0.032527 | 0.0309 | 0.029355 | 0.027888 | 0.026493 | 0.025169 | 0.02391 | 0.022715 | 0.021579 | 0.0205 | 0.019475 | 0.018501 | 0.017576 | 0.016697 | 0.015862 | 0.015069 | 0.014316 | 0.0136 | 0.01292 | 0.012274 | 0.01166 | 0.011077 | 0.010523 | 0.0099973 | 0.0094975 | 0.0090226 | 0.0085715 | 0.0081429 | 0.0077357 | 0.007349 | 0.0069815 | 0.0066324 | 0.0063008 | 0.0059858 | 0.0056865 | 0.0054022 | 0.005132 | 0.0048754 | 0.0046317 | 0.0044001 | 0.0041801 | 0.0039711 | 0.0037725 | 0.0035839
Total Leakage m³/s |  | 2.25 | 4.3875 | 6.4181 | 8.3472 | 10.1799 | 11.9209 | 13.5748 | 15.1461 | 16.6388 | 18.0568 | 19.404 | 20.6838 | 21.8996 | 23.0546 | 24.1519 | 25.1943 | 26.1846 | 27.1254 | 28.0191 | 28.8681 | 29.6747 | 30.441 | 31.1689 | 31.8605 | 32.5175 | 33.1416 | 33.7345 | 34.2978 | 34.8329 | 35.3413 | 35.8242 | 36.283 | 36.7188 | 37.1329 | 37.5262 | 37.8999 | 38.2549 | 38.5922 | 38.9126 | 39.217 | 39.5061 | 39.7808 | 40.0418 | 40.2897 | 40.5252 | 40.7489 | 40.9615 | 41.1634 | 41.3552 | 41.5375 | 41.7106 | 41.8751 | 42.0313 | 42.1798 | 42.3208 | 42.4547 | 42.582 | 42.7029 | 42.8177 | 42.9269 | 43.0305 | 43.129 | 43.2225 | 43.3114 | 43.3958 | 43.4761 | 43.5522 | 43.6246 | 43.6934 | 43.7587 | 43.8208 | 43.8798 | 43.9358 | 43.989 | 44.0395 | 44.0876 | 44.1332 | 44.1765 | 44.2177 | 44.2568 | 44.294 | 44.3293 | 44.3628 | 44.3947 | 44.4249 | 44.4537 | 44.481 | 44.507 | 44.5316 | 44.555 | 44.5773 | 44.5984 | 44.6185 | 44.6376 | 44.6557 | 44.6729 | 44.6893 | 44.7048 | 44.7196 | 44.7336 | 44.7469 | 44.7596 | 44.7716 | 44.783 | 44.7938 | 44.8042 | 44.8139 | 44.8232 | 44.8321 | 44.8405 | 44.8485 | 44.856 | 44.8632 | 44.8701 | 44.8766 | 44.8827 | 44.8886 | 44.8942 | 44.8995 | 44.9045 | 44.9093 | 44.9138 | 44.9181 | 44.9222 | 44.9261 | 44.9298 | 44.9333 | 44.9366 | 44.9398 | 44.9428 | 44.9457 | 44.9484 | 44.951 | 44.9534 | 44.9558 | 44.958 | 44.9601 | 44.9621 | 44.964 | 44.9658 | 44.9675 | 44.9691 | 44.9706 | 44.9721 | 44.9735 | 44.9748 | 44.9761 | 44.9773 | 44.9784 | 44.9795 | 44.9805 | 44.9815 | 44.9824 | 44.9833 | 44.9841 | 44.9849 | 44.9857 | 44.9864 | 44.9871 | 44.9877 | 44.9883 | 44.9889 | 44.9895 | 44.99 | 44.9905 | 44.991 | 44.9914 | 44.9919 | 44.9923 | 44.9927 | 44.993 | 44.9934 | 44.9937 | 44.994 | 44.9943 | 44.9946 | 44.9949 | 44.9951 | 44.9954 | 44.9956 | 44.9958 | 44.996 | 44.9962 | 44.9964
Leakage per section m³/s |  | 2.25 | 2.1375 | 2.0306 | 1.9291 | 1.8326 | 1.741 | 1.654 | 1.5713 | 1.4927 | 1.4181 | 1.3472 | 1.2798 | 1.2158 | 1.155 | 1.0973 | 1.0424 | 0.99029 | 0.94077 | 0.89373 | 0.84905 | 0.80659 | 0.76626 | 0.72795 | 0.69155 | 0.65698 | 0.62413 | 0.59292 | 0.56327 | 0.53511 | 0.50835 | 0.48294 | 0.45879 | 0.43585 | 0.41406 | 0.39336 | 0.37369 | 0.355 | 0.33725 | 0.32039 | 0.30437 | 0.28915 | 0.27469 | 0.26096 | 0.24791 | 0.23552 | 0.22374 | 0.21255 | 0.20193 | 0.19183 | 0.18224 | 0.17313 | 0.16447 | 0.15625 | 0.14843 | 0.14101 | 0.13396 | 0.12726 | 0.1209 | 0.11486 | 0.10911 | 0.10366 | 0.098474 | 0.09355 | 0.088873 | 0.084429 | 0.080208 | 0.076197 | 0.072388 | 0.068768 | 0.06533 | 0.062063 | 0.05896 | 0.056012 | 0.053212 | 0.050551 | 0.048023 | 0.045622 | 0.043341 | 0.041174 | 0.039115 | 0.03716 | 0.035302 | 0.033537 | 0.03186 | 0.030267 | 0.028753 | 0.027316 | 0.02595 | 0.024652 | 0.02342 | 0.022249 | 0.021136 | 0.02008 | 0.019076 | 0.018122 | 0.017216 | 0.016355 | 0.015537 | 0.01476 | 0.014022 | 0.013321 | 0.012655 | 0.012022 | 0.011421 | 0.01085 | 0.010308 | 0.0097923 | 0.0093027 | 0.0088376 | 0.0083957 | 0.0079759 | 0.0075771 | 0.0071982 | 0.0068383 | 0.0064964 | 0.0061716 | 0.005863 | 0.0055699 | 0.0052914 | 0.0050268 | 0.0047755 | 0.0045367 | 0.0043099 | 0.0040944 | 0.0038896 | 0.0036952 | 0.0035104 | 0.0033349 | 0.0031681 | 0.0030097 | 0.0028592 | 0.0027163 | 0.0025805 | 0.0024514 | 0.0023289 | 0.0022124 | 0.0021018 | 0.0019967 | 0.0018969 | 0.001802 | 0.0017119 | 0.0016263 | 0.001545 | 0.0014678 | 0.0013944 | 0.0013247 | 0.0012584 | 0.0011955 | 0.0011357 | 0.0010789 | 0.001025 | 0.00097375 | 0.00092506 | 0.00087881 | 0.00083487 | 0.00079312 | 0.00075347 | 0.00071579 | 0.00068001 | 0.000646 | 0.0006137 | 0.00058302 | 0.00055387 | 0.00052617 | 0.00049987 | 0.00047487 | 0.00045113 | 0.00042857 | 0.00040714 | 0.00038679 | 0.00036745 | 0.00034908 | 0.00033162 | 0.00031504 | 0.00029929 | 0.00028432 | 0.00027011 | 0.0002566 | 0.00024377 | 0.00023158 | 0.00022 | 0.000209 | 0.00019855 | 0.00018863
w = air density | 1.2 | Kg/m³ | 1.2 | Kg/m³
Duct Velocity - m/s | 38.4949 | 36.5701 | 34.7416 | 33.0045 | 31.3543 | 29.7866 | 28.2973 | 26.8824 | 25.5383 | 24.2614 | 23.0483 | 21.8959 | 20.8011 | 19.761
Fan Velocity @ motor - m/s | 59.6671 | 56.6837 | 53.8495 | 51.157 | 48.5992 | 46.1692 | 43.8608 | 41.6677 | 39.5843 | 37.6051 | 35.7249 | 33.9386 | 32.2417 | 30.6296
K = | 0.0037 | ns²/m⁴ | 0.55 | 55 | % motor Occupying fan casing
C = | 3.8327 | m
A = | 1.169 | m² | 110 | 160 | 210 | 260 | 310 | 360 | 410 | 460 | 510 | 560 | 610 | 660 | 710 | 760 | 810 | 860 | 910 | 960 | 1010 | 1060 | 1110 | 1160 | 1210 | 1260 | 1310 | 1360 | 1410 | 1460 | 1510 | 1560 | 1610 | 1660 | 1710 | 1760 | 1810 | 1860 | 1910 | 1960 | 2010 | 2060 | 2110 | 2160 | 2210 | 2260 | 2310 | 2360 | 2410 | 2460 | 2510 | 2560 | 2610 | 2660 | 2710 | 2760 | 2810 | 2860 | 2910 | 2960 | 3010 | 3060 | 3110 | 3160 | 3210 | 3260 | 3310
P Drop per pipe Section (Pa) | 179.7661 | 973.4335 | 1610.6268 | 2114.3138 | 2504.4708 | 2798.4479 | 3011.2914 | 3156.0277 | 3243.9143 | 3284.661 | 3286.6247 | 3256.9806 | 3201.8736 | 3126.5509 | 3035.4782 | 2932.443 | 2820.6436 | 2702.7686 | 2581.0654 | 2457.4012 | 2333.3152 | 2210.0653 | 2088.6681 | 1969.9339 | 1854.4975 | 1742.8445 | 1635.3345 | 1532.221 | 1433.6688 | 1339.7686 | 1250.5501 | 1165.993 | 1086.0365 | 1010.5874 | 939.5266 | 872.7159 | 810.0018 | 751.2207 | 696.2019 | 644.7704 | 596.7498 | 551.9639 | 510.2384 | 471.4022 | 435.2887 | 401.736 | 370.5881 | 341.6951 | 314.9133 | 290.1057 | 267.1419 | 245.8983 | 226.2577 | 208.1094 | 191.3491 | 175.8788 | 161.6062 | 148.4448 | 136.3136 | 125.1368 | 114.8436 | 105.3681 | 96.6485 | 88.6276 | 81.2521 | 74.4722 | 68.242 | 62.5187 | 57.2628 | 52.4374 | 48.0087 | 43.945 | 40.2174 | 36.7989 | 33.6647 | 30.7919 | 28.1592 | 25.7472 | 23.5379 | 21.5146 | 19.6621 | 17.9663 | 16.4142 | 14.9941 | 13.6948 | 12.5063 | 11.4195 | 10.4256 | 9.517 | 8.6865 | 7.9274 | 7.2338 | 6.6001 | 6.0212 | 5.4925 | 5.0096 | 4.5686 | 4.166 | 3.7985 | 3.4631 | 3.1569 | 2.8776 | 2.6227 | 2.3901 | 2.178 | 1.9845 | 1.808 | 1.6471 | 1.5004 | 1.3666 | 1.2447 | 1.1335 | 1.0322 | 0.93985 | 0.85571 | 0.77904 | 0.70919 | 0.64555 | 0.58758 | 0.53478 | 0.48668 | 0.44289 | 0.403 | 0.36669 | 0.33362 | 0.30352 | 0.27611 | 0.25117 | 0.22846 | 0.20779 | 0.18898 | 0.17187 | 0.15629 | 0.14212 | 0.12923 | 0.1175 | 0.10683 | 0.097118 | 0.088288 | 0.080256 | 0.072952 | 0.066309 | 0.060267 | 0.054774 | 0.049778 | 0.045237 | 0.041107 | 0.037353 | 0.03394 | 0.030838 | 0.028017 | 0.025454 | 0.023124 | 0.021007 | 0.019082 | 0.017334 | 0.015744 | 0.0143 | 0.012988 | 0.011796 | 0.010713 | 0.0097285 | 0.0088344 | 0.0080222 | 0.0072844 | 0.0066142 | 0.0060055 | 0.0054525 | 0.0049503 | 0.0044942 | 0.00408 | 0.0037039 | 0.0033623 | 0.0030521 | 0.0027704 | 0.0025146 | 0.0022824 | 0.0020716 | 0.0018801 | 0.0017063 | 0.0015486 | 0.0014053 | 0.0012753 | 0.0011573 | 0.0010502
P Drop TOTAL (Leakless) = Pa | 179.7661 | 1153.1996 | 2763.8265 | 4878.1402 | 7382.611 | 10181.0589 | 13192.3503 | 16348.378 | 19592.2922 | 22876.9532 | 26163.5779 | 29420.5585 | 32622.4321 | 35748.983 | 38784.4612 | 41716.9042 | 44537.5478 | 47240.3164 | 49821.3818 | 52278.783 | 54612.0982 | 56822.1635 | 58910.8316 | 60880.7656 | 62735.2631 | 64478.1075 | 66113.442 | 67645.6631 | 69079.3319 | 70419.1005 | 71489.8844 | 71682.444 | 71157.8537 | 70054.1272 | 68489.1831 | 66563.4511 | 64362.1615 | 61957.3545 | 59409.6421 | 56769.7516 | 54079.8768 | 51374.8601 | 48683.2248 | 46028.0762 | 43427.8866 | 40897.1796 | 38447.1241 | 36086.0507 | 33819.8985 | 31652.6031 | 29586.4298 | 27622.2627 | 25759.8523 | 23998.0277 | 22334.8794 | 20767.9137 | 19294.1853 | 17910.4091 | 16613.0538 | 15398.422 | 14262.7156 | 13202.0906 | 12212.7026 | 11290.7429 | 10432.4683 | 9634.2246 | 8892.4648 | 8203.7628 | 7564.8237 | 6972.4908 | 6423.7496 | 5915.7307 | 5445.7097 | 5011.1065 | 4609.4825 | 4238.5384 | 3896.1095 | 3580.1617 | 3288.7863 | 3020.1951 | 2772.7153 | 2544.7832 | 2334.9398 | 2141.8245 | 1964.1702 | 1800.7977 | 1650.611 | 1512.5919 | 1385.7953 | 1269.3451 | 1162.4289 | 1064.2946 | 974.2462 | 891.6398 | 815.8802 | 746.4176 | 682.7442 | 624.3915 | 570.9272 | 521.9529 | 477.1011 | 436.0337 | 398.4389 | 364.0301 | 332.5434 | 303.736 | 277.3848 | 253.2847 | 231.2472 | 211.0992 | 192.6819 | 175.8491 | 160.467 | 146.4128 | 133.5737 | 121.8464 | 111.1361 | 101.3561 | 92.4266 | 84.2749 | 76.8342 | 70.0432 | 63.8461 | 58.1916 | 53.0327 | 48.3267 | 44.0342 | 40.1193 | 36.5492 | 33.2939 | 30.326 | 27.6203 | 25.1539 | 22.9059 | 20.8571 | 18.9901 | 17.2889 | 15.7389 | 14.3268 | 13.0405 | 11.8687 | 10.8015 | 9.8296 | 8.9446 | 8.1386 | 7.4048 | 6.7367 | 6.1285 | 5.5749 | 5.071 | 4.6123 | 4.1949 | 3.815 | 3.4693 | 3.1548 | 2.8686 | 2.6082 | 2.3714 | 2.1559 | 1.9599 | 1.7816 | 1.6195 | 1.472 | 1.3379 | 1.216 | 1.1051 | 1.0043 | 0.9126 | 0.82926 | 0.7535 | 0.68463 | 0.62202 | 0.56512 | 0.5134 | 0.46639 | 0.42367 | 0.38484 | 0.34956 | 0.3175 | 0.28837 | 0.2619 | 0.23785 | 0.216 | 0.19615 | 0.17812
P Drop per pipe Section = kPa | 179.7661 | 180.9193 | 1.6106 | 2.1143 | 2.5045 | 2.7984 | 3.0113 | 3.156 | 3.2439 | 3.2847 | 3.2866 | 3.257 | 3.2019 | 3.1266 | 3.0355 | 2.9324 | 2.8206 | 2.7028 | 2.5811 | 2.4574 | 2.3333 | 2.2101 | 2.0887 | 1.9699 | 1.8545 | 1.7428 | 1.6353 | 1.5322 | 1.4337 | 1.3398 | 1.2506 | 1.166 | 1.086 | 1.0106 | 0.93953 | 0.87272 | 0.81 | 0.75122 | 0.6962 | 0.64477 | 0.59675 | 0.55196 | 0.51024 | 0.4714 | 0.43529 | 0.40174 | 0.37059 | 0.3417 | 0.31491 | 0.29011 | 0.26714 | 0.2459 | 0.22626 | 0.20811 | 0.19135 | 0.17588 | 0.16161 | 0.14844 | 0.13631 | 0.12514 | 0.11484 | 0.10537 | 0.096649 | 0.088628 | 0.081252 | 0.074472 | 0.068242 | 0.062519 | 0.057263 | 0.052437 | 0.048009 | 0.043945 | 0.040217 | 0.036799 | 0.033665 | 0.030792 | 0.028159 | 0.025747 | 0.023538 | 0.021515 | 0.019662 | 0.017966 | 0.016414 | 0.014994 | 0.013695 | 0.012506 | 0.011419 | 0.010426 | 0.009517 | 0.0086865 | 0.0079274 | 0.0072338 | 0.0066001 | 0.0060212 | 0.0054925 | 0.0050096 | 0.0045686 | 0.004166 | 0.0037985 | 0.0034631 | 0.0031569 | 0.0028776 | 0.0026227 | 0.0023901 | 0.002178 | 0.0019845 | 0.001808 | 0.0016471 | 0.0015004 | 0.0013666 | 0.0012447 | 0.0011335 | 0.0010322 | 0.00093985 | 0.00085571 | 0.00077904 | 0.00070919 | 0.00064555 | 0.00058758 | 0.00053478 | 0.00048668 | 0.00044289 | 0.000403 | 0.00036669 | 0.00033362 | 0.00030352 | 0.00027611 | 0.00025117 | 0.00022846 | 0.00020779 | 0.00018898 | 0.00017187 | 0.00015629 | 0.00014212 | 0.00012923 | 0.0001175 | 0.00010683 | 9.7118e-05 | 8.8288e-05 | 8.0256e-05 | 7.2952e-05 | 6.6309e-05 | 6.0267e-05 | 5.4774e-05 | 4.9778e-05 | 4.5237e-05 | 4.1107e-05 | 3.7353e-05 | 3.394e-05 | 3.0838e-05 | 2.8017e-05 | 2.5454e-05 | 2.3124e-05 | 2.1007e-05 | 1.9082e-05 | 1.7334e-05 | 1.5744e-05 | 1.43e-05 | 1.2988e-05 | 1.1796e-05 | 1.0713e-05 | 9.7285e-06 | 8.8344e-06 | 8.0222e-06 | 7.2844e-06 | 6.6142e-06 | 6.0055e-06 | 5.4525e-06 | 4.9503e-06 | 4.4942e-06 | 4.08e-06 | 3.7039e-06 | 3.3623e-06 | 3.0521e-06 | 2.7704e-06 | 2.5146e-06 | 2.2824e-06 | 2.0716e-06 | 1.8801e-06 | 1.7063e-06 | 1.5486e-06 | 1.4053e-06 | 1.2753e-06 | 1.1573e-06 | 1.0502e-06
P Drop TOTAL = kPa |  | 1.0786 | 1.9774 | 2.8763 | 3.7751 | 4.6739 | 5.5727 | 6.4716 | 7.3704 | 8.2692 | 9.1681 | 10.0669 | 10.9657 | 11.8646 | 12.7634 | 13.6622 | 14.5611 | 15.4599 | 16.3587 | 17.2575 | 18.1564 | 19.0552 | 19.954 | 20.8529 | 21.7517 | 22.6505 | 23.5494 | 24.4482 | 25.347 | 26.2459 | 27.1447 | 28.0435 | 28.9423 | 29.8412 | 30.74 | 31.6388 | 32.5377 | 33.4365 | 34.3353 | 35.2342 | 36.133 | 37.0318 | 37.9306
| 1.2 | Kg/m³
Max Fan Pressure kPa (Check line "17") | 1.0786 | kPa
Max Fan Pressure kPa (85%) | 0.91681 | kPa | Note!!!! - Rule of thumb - a fan will do ±85% of it's max Pressure (depicted on a curve)
Air Density at fan | 1.2 | Kg/m³
Fan Pressure Capability Pa | 1100.1686 | Pa
Fan Pressure Capability kPa | 1.1002 | kPa
Air Speed in duct = km/hr | 138.5816 | 131.6525 | 125.0699 | 118.8164 | 112.8756 | 107.2318 | 101.8702 | 96.7767 | 91.9378 | 87.341 | 82.9739 | 78.8252 | 74.8839 | 71.1398
R =XXXXX Ns2/m8 | 0.088773 | 0.53264 | 0.97651 | 1.4204 | 1.8642 | 2.3081 | 2.752 | 3.1958 | 3.6397 | 4.0836 | 4.5274 | 4.9713 | 5.4152 | 5.859 | 6.3029 | 6.7468 | 7.1906 | 7.6345 | 8.0784 | 8.5222 | 8.9661 | 9.41 | 9.8538 | 10.2977 | 10.7416 | 11.1854 | 11.6293 | 12.0732 | 12.517 | 12.9609 | 13.4048 | 13.8486 | 14.2925 | 14.7364 | 15.1802 | 15.6241 | 16.068 | 16.5119 | 16.9557 | 17.3996 | 17.8435 | 18.2873 | 18.7312 | 19.1751 | 19.6189 | 20.0628 | 20.5067 | 20.9505 | 21.3944 | 21.8383 | 22.2821 | 22.726 | 23.1699 | 23.6137 | 24.0576 | 24.5015 | 24.9453 | 25.3892 | 25.8331 | 26.2769 | 26.7208 | 27.1647 | 27.6085 | 28.0524 | 28.4963 | 28.9401 | 29.384 | 29.8279 | 30.2717 | 30.7156 | 31.1595 | 31.6033 | 32.0472 | 32.4911 | 32.9349 | 33.3788 | 33.8227 | 34.2665 | 34.7104 | 35.1543 | 35.5981 | 36.042 | 36.4859 | 36.9297 | 37.3736 | 37.8175 | 38.2613 | 38.7052 | 39.1491 | 39.5929 | 40.0368 | 40.4807 | 40.9245 | 41.3684 | 41.8123 | 42.2561 | 42.7 | 43.1439 | 43.5877 | 44.0316 | 44.4755 | 44.9193 | 45.3632 | 45.8071 | 46.2509 | 46.6948 | 47.1387 | 47.5825 | 48.0264 | 48.4703 | 48.9141 | 49.358 | 49.8019 | 50.2457 | 50.6896 | 51.1335 | 51.5773 | 52.0212 | 52.4651 | 52.9089 | 53.3528 | 53.7967 | 54.2405 | 54.6844 | 55.1283 | 55.5721 | 56.016 | 56.4599 | 56.9037 | 57.3476 | 57.7915 | 58.2353 | 58.6792 | 59.1231 | 59.5669 | 60.0108 | 60.4547 | 60.8985 | 61.3424 | 61.7863 | 62.2301 | 62.674 | 63.1179 | 63.5617 | 64.0056 | 64.4495 | 64.8933 | 65.3372 | 65.7811 | 66.2249 | 66.6688 | 67.1127 | 67.5565 | 68.0004 | 68.4443 | 68.8881 | 69.332 | 69.7759 | 70.2198 | 70.6636 | 71.1075 | 71.5514 | 71.9952 | 72.4391 | 72.883 | 73.3268 | 73.7707 | 74.2146 | 74.6584 | 75.1023 | 75.5462 | 75.99 | 76.4339 | 76.8778 | 77.3216 | 77.7655 | 78.2094 | 78.6532 | 79.0971 | 79.541 | 79.9848 | 80.4287 | 80.8726 | 81.3164 | 81.7603
Pressure | 179.7661 | 973.4335 | 1610.6268 | 2114.3138 | 2504.4708 | 2798.4479 | 3011.2914 | 3156.0277 | 3243.9143 | 3284.661 | 3286.6247 | 3256.9806
Velocity Pressure VP | 889.1135 | 802.4249 | 724.1885 | 653.5801 | 589.856 | 532.3451 | 480.4414 | 433.5984 | 391.3226 | 353.1686 | 318.7347 | 287.658
Air Power ~ kW (P x Q / 1000) | 8.0895 | 41.6143 | 65.4116 | 81.5742 | 91.7958 | 97.4424 | 99.6109 | 99.1787 | 96.8436 | 93.157 | 88.5521 | 83.3657
Air Power ~ W (P x Q) | 8089.4751 | 41614.2821 | 65411.5827 | 81574.1901 | 91795.8185 | 97442.3542 | 99610.915 | 99178.7322 | 96843.5552 | 93157.0045 | 88552.0614 | 83365.6887
Air Power ~ kW (R x Q³ / 1000) | 8.0895 | 41.6143 | 65.4116 | 81.5742 | 91.7958 | 97.4424 | 99.6109 | 99.1787 | 96.8436 | 93.157 | 88.5521 | 83.3657
Air Power ~ W (R x Q³) | 8089.4751 | 41614.2821 | 65411.5827 | 81574.1901 | 91795.8185 | 97442.3542 | 99610.915 | 99178.7322 | 96843.5552 | 93157.0045 | 88552.0614 | 83365.6887
FAN Selection (kW) |  |  |  | Fan Speed | Fan rpm | Fan Speed | Fan rpm | Fan Speed | Fan rpm | Fan Speed | Fan rpm
Fan efficiency | 0.72 | % |  | 100% | 1470 | 40% | 588 | 50% | 735 | 70% | 1029
Motor electrical efficiency | 0.9 | % |  | Volume (m³/s) | SP (Pa) @ Design kg/m³ | Volume (m³/s) | SP (Pa) @ Design kg/m³ | Volume (m³/s) | SP (Pa) @ Design kg/m³ | Volume (m³/s) | SP (Pa) @ Design kg/m³
Fan kW Required | 150.5354 | kW |  | 25 | 1480 | 10 | 243.3105 | 12.5 | 370 | 17.5 | 725.2
Dynamic Pressure | 889.1135 | Pa |  | 27.5 | 1320 | 11 | 211.2 | 13.75 | 330 | 19.25 | 646.8
Anticipated Shock Losses (Bends / Reducers etc.) | 200 | Pa |  | 30 | 1140 | 12 | 182.4 | 15 | 285 | 21 | 558.6
Fan Total Pressure | 2.1677 | kPa |  | 32.5 | 950 | 13 | 152 | 16.25 | 237.5 | 22.75 | 465.5
|  |  |  | 35 | 550 | 14 | 88 | 17.5 | 137.5 | 24.5 | 269.5
Leakage |  |  |  | 38 | 0 | 15.2 | 0 | 19 | 0 | 26.6 | 0
Parameters | ENTER |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Qty in m³/s | 27.5
Qty out m³/s | 18
Length of column m | 500
Leakage if Column is < 100m long | 34.5455 | %/100m
Leakage if Column is > 100m long | 6.9091 | %/100m | [5 empty] | Typical air quantities and pressures of fans generally in use
525V Fans
Pipe Diameter = | 1.4 | m | Enter |  |  |  |  | 300 mm Ø x 0,75 kW fan handles approximately 0,95 m³ / s at 250 Pa
L = (in meters) | 800 | m | Enter |  |  |  |  | 300 mm Ø x 1,5 kW fan handles approximately 1,8 m³ / s at 370 Pa
Qty (m³/s) | 30 | m³/s | Enter |  |  |  |  | 406 mm Ø x 4,0 kW fan handles approximately 2,0 m³ / s at 900 Pa
w = air density | 1 | Kg/m³ | Enter | 1.2 | Kg/m³ |  |  | 570 mm Ø x 8,0 kW fan handles approximately 4,0 m³ / s at 900 Pa
K = | 0.004 | ns²/m⁴ | Enter |  |  |  |  | 570 mm Ø x 15,0 kW fan handles approximately 6,8 m³ / s at 1100 Pa
C = | 4.3982 | m | [5 empty] | 760 mm Ø x 22,0 kW fan handles approximately 9,0 m³ / s at 950 Pa
A = | 1.5394 | m² | [5 empty] | 760 mm Ø x 41,0 kW fan handles approximately 11,8 m³ / s at 1900 Pa
P Drop = | 2893.6853 | Pa | [5 empty] | 760 mm Ø x 45,0 kW fan handles approximately 12,8 m³ / s at 1400 Pa
P Drop = kPa | 2.8937 | kPa | [5 empty] | 1015 mm Ø x 75,0 kW fan handles approximately 22,0 m³ / s at 2200 Pa
R = | 3.2152 | Ns2/m8 | R =
Fan Air Power Required | [7 empty] | Spacing of fans in ventilation columns
Parameters | ENTER | [6 empty] | 406 mm Ø x 4,00 kW fan in a 406 mm column Max 100 metres apart
Qty in m³/s | 170 | m³/s | [5 empty] | 570 mm Ø x 8,00 kW fan in a 570 mm column Max 175 metres apart
Pressure | 3.9 | kPa | [5 empty] | 570 mm Ø x 11,0/15 kW fan in a 570 mm column Max 200 metres apart
Fan Efficiency | 87 | % | [5 empty] | 760 mm Ø x 22,0 kW fan in a 760 mm column Max 220 metres apart
Fan Input Power | 762.069 | kW | [5 empty] | 760 mm Ø x 41,0/45 kW fan in a 760 mm column Max 180 metres apart
1016 mm Ø x 75,0 kW fan in a 760 mm column Max 130 metres apart
K Factors | [7 empty] | Notes: Fan in Series
6 Swage standard galvanized Duct | 0.0037 | ns²/m⁴ | [5 empty] | Installation of multiple fans in a long ventilation column is a practice that should be avoided in future.
Mild Steel smooth Bore vent Duct (Sinking Duct) | 0.00275 | ns²/m⁴ | [5 empty] | Twin haulage development or custom designed centrifugal fans should be used instead.
K Factor on Smooth bore pipes | 0.002 | ns²/m⁴ | [5 empty] | Where multiple fans are unavoidable, a risk assessment will be conducted and a control system to detect and prevent re-circulation will be implemented
Spiral duct (Energy efficient) | 0.0025 | ns²/m⁴ | [5 empty] | Where one fan feeds another always cater for the maximum Qty the fed (2'nd) fan can deliver + an overlap Qty of at least 1.5 times or 0.3m/s x area (Allow for feed fan leakage as well)
LHPC Ducting Type A | 0.0015 | ns²/m⁴
LHPC Ducting Type B | 0.002 | ns²/m⁴ | [5 empty] | Notes | Ideal velocity in an upcast shaft <7m/s and >13m/s (Water blanket)
ABC Ducting 1200/1400mm diameter | 0.003 | ns²/m⁴ | [6 empty] | Economical velocity in an upcast shaft 18 - 25.0m/s (Ideally 22m/s)
ABC Spiral Ducting 1200/1400mm diameter | 0.005 | ns²/m⁴ | [6 empty] | Ideal velocity in an downcast shaft <13m/s (Conveyance interference)
Flexible ducting - Force | 0.005 | ns²/m⁴ | [6 empty] | Ideal velocity in a duct 25.0 - 28.0m/s
Flexible ducting - Exhaust (Spiral) | 0.0065 | ns²/m⁴ | [6 empty] | Ideal velocity in a intake airway <7m/s
Ideal velocity in a return airway <12m/s
Ideal velocity in a Vent hole <15m/s
Duct Diameter vs Distance
Pressure Drop - kPa
w = air density | 1.3 | Kg/m³ | 1.2 | Kg/m³
K = | 0.0037 | ns²/m⁴
Leakage Allowed | 10% | /100m
0,57m Pipe Diameter (in meters)
m Pipe Diameter (in meters) | 0.57
C = | 1.7907 | m
A = | 0.25518 | m²
Qty (m³/s) | 4 | 5 | 6 | 7 | 8 | m³/s
Fan Pressure | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | (Max x 0.85)
Duct Length m | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Qty (m³/s) | 4 | 3.96 | 3.9204 | 3.8812 | 3.8424 | 3.804 | 3.7659 | 3.7283 | 3.691 | 3.6541 | 3.6175
| 5 | 4.95 | 4.9005 | 4.8515 | 4.803 | 4.755 | 4.7074 | 4.6603 | 4.6137 | 4.5676 | 4.5219
| 6 | 5.94 | 5.8806 | 5.8218 | 5.7636 | 5.7059 | 5.6489 | 5.5924 | 5.5365 | 5.4811 | 5.4263
| 7 | 6.93 | 6.8607 | 6.7921 | 6.7242 | 6.6569 | 6.5904 | 6.5245 | 6.4592 | 6.3946 | 6.3307
| 8 | 7.92 | 7.8408 | 7.7624 | 7.6848 | 7.6079 | 7.5318 | 7.4565 | 7.382 | 7.3081 | 7.2351
4.0 m³/s | 0 | 0.067742 | 0.13279 | 0.19522 | 0.25511 | 0.31254 | 0.36759 | 0.42032 | 0.47081 | 0.51912 | 0.56532
5.0 m³/s | 0 | 0.10585 | 0.20748 | 0.30503 | 0.39861 | 0.48835 | 0.57436 | 0.65675 | 0.73564 | 0.81112 | 0.88331
6.0 m³/s | 0 | 0.15242 | 0.29877 | 0.43924 | 0.574 | 0.70322 | 0.82708 | 0.94572 | 1.0593 | 1.168 | 1.272
7.0 m³/s | 0 | 0.20746 | 0.40666 | 0.59786 | 0.78128 | 0.95717 | 1.1257 | 1.2872 | 1.4418 | 1.5898 | 1.7313
8.0 m³/s | 0 | 0.27097 | 0.53115 | 0.78088 | 1.0204 | 1.2502 | 1.4704 | 1.6813 | 1.8832 | 2.0765 | 2.2613
0,6m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 0.6 | m
C = | 1.885 | m
A = | 0.28274 | m²
Qty (m³/s) | 6 | 7 | 8 | 9 | 10 | m³/s
Fan Pressure | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | (Max x 0.85)
Duct Length m | 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140
Qty (m³/s) | 6 | 5.88 | 5.7624 | 5.6472 | 5.5342 | 5.4235 | 5.3151 | 5.2088
| 7 | 6.86 | 6.7228 | 6.5883 | 6.4566 | 6.3274 | 6.2009 | 6.0769
| 8 | 7.84 | 7.6832 | 7.5295 | 7.3789 | 7.2314 | 7.0867 | 6.945
| 9 | 8.82 | 8.6436 | 8.4707 | 8.3013 | 8.1353 | 7.9726 | 7.8131
| 10 | 9.8 | 9.604 | 9.4119 | 9.2237 | 9.0392 | 8.8584 | 8.6813
6m³/s | 0 | 0.23114 | 0.44397 | 0.63958 | 0.81901 | 0.98322 | 1.1331 | 1.2696
7m³/s | 0 | 0.31461 | 0.60429 | 0.87055 | 1.1148 | 1.3383 | 1.5423 | 1.7281 | 6m³/s
8m³/s | 0 | 0.41091 | 0.78928 | 1.137 | 1.456 | 1.7479 | 2.0145 | 2.2572
9m³/s | 0 | 0.52006 | 0.99893 | 1.4391 | 1.8428 | 2.2122 | 2.5496 | 2.8567
10m³/s | 0 | 0.64205 | 1.2333 | 1.7766 | 2.275 | 2.7312 | 3.1476 | 3.5268
0,76m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 0.76 | m
C = | 2.3876 | m
A = | 0.45365 | m²
Qty (m³/s) | 10 | 11 | 12 | 13 | 14 | m³/s
Duct Velocity | 22.0436 | 24.248 | 26.4523 | 28.6567 | 30.8611 | m/s
Fan Pressure | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | 1.615 | (Max x 0.85)
Duct Length m | 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160
Qty (m³/s) | 10 | 9.8 | 9.604 | 9.4119 | 9.2237 | 9.0392 | 8.8584 | 8.6813 | 8.5076
| 11 | 10.78 | 10.5644 | 10.3531 | 10.146 | 9.9431 | 9.7443 | 9.5494 | 9.3584
| 12 | 11.76 | 11.5248 | 11.2943 | 11.0684 | 10.847 | 10.6301 | 10.4175 | 10.2092
| 13 | 12.74 | 12.4852 | 12.2355 | 11.9908 | 11.751 | 11.516 | 11.2856 | 11.0599
| 14 | 13.72 | 13.4456 | 13.1767 | 12.9132 | 12.6549 | 12.4018 | 12.1538 | 11.9107
10m³/s | 0 | 0.19691 | 0.37822 | 0.54486 | 0.69771 | 0.8376 | 0.96532 | 1.0816 | 1.1872
11m³/s | 0 | 0.23826 | 0.45764 | 0.65928 | 0.84423 | 1.0135 | 1.168 | 1.3087 | 1.4365
12m³/s | 0 | 0.28354 | 0.54463 | 0.7846 | 1.0047 | 1.2061 | 1.3901 | 1.5575 | 1.7095
13m³/s | 0 | 0.33277 | 0.63919 | 0.92081 | 1.1791 | 1.4155 | 1.6314 | 1.8279 | 2.0063
14m³/s | 0 | 0.38594 | 0.7413 | 1.0679 | 1.3675 | 1.6417 | 1.892 | 2.1199 | 2.3269
0,8m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 0.8 | m
C = | 2.5133 | m
A = | 0.50265 | m²
Qty (m³/s) | 11 | 12 | 13 | 14 | 15 | m³/s
Fan Pressure | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | (Max x 0.85)
Duct Length m | 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200
Qty (m³/s) | 11 | 10.78 | 10.5644 | 10.3531 | 10.146 | 9.9431 | 9.7443 | 9.5494 | 9.3584 | 9.1712 | 8.9878
| 12 | 11.76 | 11.5248 | 11.2943 | 11.0684 | 10.847 | 10.6301 | 10.4175 | 10.2092 | 10.005 | 9.8049
| 13 | 12.74 | 12.4852 | 12.2355 | 11.9908 | 11.751 | 11.516 | 11.2856 | 11.0599 | 10.8387 | 10.6219
| 14 | 13.72 | 13.4456 | 13.1767 | 12.9132 | 12.6549 | 12.4018 | 12.1538 | 11.9107 | 11.6725 | 11.439
| 15 | 14.7 | 14.406 | 14.1179 | 13.8355 | 13.5588 | 13.2876 | 13.0219 | 12.7614 | 12.5062 | 12.2561
11m³/s | 0 | 0.18436 | 0.35411 | 0.51014 | 0.65325 | 0.78422 | 0.9038 | 1.0127 | 1.1115 | 1.2009 | 1.2815
12m³/s | 0 | 0.2194 | 0.42143 | 0.60711 | 0.77742 | 0.93329 | 1.0756 | 1.2052 | 1.3228 | 1.4292 | 1.5251
13m³/s | 0 | 0.25749 | 0.49459 | 0.71251 | 0.91239 | 1.0953 | 1.2623 | 1.4144 | 1.5525 | 1.6773 | 1.7899
14m³/s | 0 | 0.29863 | 0.57361 | 0.82634 | 1.0582 | 1.2703 | 1.464 | 1.6404 | 1.8005 | 1.9453 | 2.0759
15m³/s | 0 | 0.34281 | 0.65848 | 0.9486 | 1.2147 | 1.4583 | 1.6806 | 1.8831 | 2.0669 | 2.2332 | 2.383
0,9m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 0.9 | m
C = | 2.8274 | m
A = | 0.63617 | m²
Qty (m³/s) | 16 | 18 | 20 | 22 | 24 | m³/s
Fan Pressure | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | (Max x 0.85)
Duct Length m | 0 | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200 | 220
Qty (m³/s) | 16 | 15.68 | 15.3664 | 15.0591 | 14.7579 | 14.4627 | 14.1735 | 13.89 | 13.6122 | 13.34 | 13.0732 | 12.8117
| 18 | 17.64 | 17.2872 | 16.9415 | 16.6026 | 16.2706 | 15.9452 | 15.6263 | 15.3137 | 15.0075 | 14.7073 | 14.4132
| 20 | 19.6 | 19.208 | 18.8238 | 18.4474 | 18.0784 | 17.7168 | 17.3625 | 17.0153 | 16.675 | 16.3415 | 16.0146
| 22 | 21.56 | 21.1288 | 20.7062 | 20.2921 | 19.8863 | 19.4885 | 19.0988 | 18.7168 | 18.3425 | 17.9756 | 17.6161
| 24 | 23.52 | 23.0496 | 22.5886 | 22.1368 | 21.6941 | 21.2602 | 20.835 | 20.4183 | 20.0099 | 19.6097 | 19.2176
16m³/s | 0 | 0.21645 | 0.41575 | 0.59893 | 0.76696 | 0.92073 | 1.0611 | 1.189 | 1.305 | 1.41 | 1.5046 | 1.5895
18m³/s | 0 | 0.27394 | 0.52619 | 0.75803 | 0.97068 | 1.1653 | 1.343 | 1.5048 | 1.6516 | 1.7845 | 1.9043 | 2.0117
20m³/s | 0 | 0.3382 | 0.64961 | 0.93583 | 1.1984 | 1.4386 | 1.658 | 1.8577 | 2.0391 | 2.2031 | 2.3509 | 2.4836
22m³/s | 0 | 0.40922 | 0.78603 | 1.1324 | 1.45 | 1.7408 | 2.0062 | 2.2479 | 2.4673 | 2.6657 | 2.8446 | 3.0052
24m³/s | 0 | 0.48701 | 0.93545 | 1.3476 | 1.7256 | 2.0716 | 2.3875 | 2.6751 | 2.9362 | 3.1725 | 3.3854 | 3.5764
1m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 1 | m
C = | 3.1416 | m
A = | 0.7854 | m²
Qty (m³/s) | 18 | 20 | 22 | 24 | 26 | m³/s
Fan Pressure | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | (Max x 0.85)
Duct Length m | 0 | 50 | 100 | 150 | 200 | 250 | 300
Qty (m³/s) | 18 | 17.1 | 16.245 | 15.4328 | 14.6611 | 13.9281 | 13.2317
| 20 | 19 | 18.05 | 17.1475 | 16.2901 | 15.4756 | 14.7018
| 22 | 20.9 | 19.855 | 18.8622 | 17.9191 | 17.0232 | 16.172
| 24 | 22.8 | 21.66 | 20.577 | 19.5482 | 18.5707 | 17.6422
| 26 | 24.7 | 23.465 | 22.2918 | 21.1772 | 20.1183 | 19.1124
18m³/s | 0 | 0.38002 | 0.68594 | 0.92859 | 1.1174 | 1.2606 | 1.3652
20m³/s | 0 | 0.46916 | 0.84683 | 1.1464 | 1.3795 | 1.5563 | 1.6854
22m³/s | 0 | 0.56768 | 1.0247 | 1.3871 | 1.6692 | 1.8831 | 2.0394
24m³/s | 0 | 0.67559 | 1.2194 | 1.6508 | 1.9865 | 2.241 | 2.427
26m³/s | 0 | 0.79288 | 1.4312 | 1.9374 | 2.3314 | 2.6301 | 2.8484
1,2m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 1.2 | m
C = | 3.7699 | m
A = | 1.131 | m²
Qty (m³/s) | 28 | 30 | 32 | 34 | 36 | m³/s
Fan Pressure | 1.785 | 1.785 | 1.785 | 1.785 | 1.785 | 1.785 | 1.785 | 1.785 | (Max x 0.85)
Duct Length m | 0 | 50 | 100 | 150 | 200 | 250 | 300 | 350
Qty (m³/s) | 28 | 26.6 | 25.27 | 24.0065 | 22.8062 | 21.6659 | 20.5826 | 19.5534
| 30 | 28.5 | 27.075 | 25.7212 | 24.4352 | 23.2134 | 22.0528 | 20.9501
| 32 | 30.4 | 28.88 | 27.436 | 26.0642 | 24.761 | 23.5229 | 22.3468
| 34 | 32.3 | 30.685 | 29.1507 | 27.6932 | 26.3086 | 24.9931 | 23.7435
| 36 | 34.2 | 32.49 | 30.8655 | 29.3222 | 27.8561 | 26.4633 | 25.1401
28m³/s | 0 | 0.36955 | 0.66703 | 0.903 | 1.0866 | 1.2258 | 1.3276 | 1.3978
30m³/s | 0 | 0.42423 | 0.76573 | 1.0366 | 1.2474 | 1.4072 | 1.524 | 1.6046
32m³/s | 0 | 0.48268 | 0.87123 | 1.1794 | 1.4192 | 1.6011 | 1.734 | 1.8257
34m³/s | 0 | 0.5449 | 0.98354 | 1.3315 | 1.6022 | 1.8075 | 1.9575 | 2.0611
36m³/s | 0 | 0.61089 | 1.1026 | 1.4927 | 1.7962 | 2.0264 | 2.1946 | 2.3107
1,4m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 1.4 | m
C = | 4.3982 | m
A = | 1.5394 | m²
Qty (m³/s) | 44 | 46 | 48 | 50 | 52 | m³/s
Fan Pressure | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | (Max x 0.85)
Duct Length m | 0 | 200 | 400 | 600 | 800 | 1000
Qty (m³/s) | 44 | 35.2 | 28.16 | 22.528 | 18.0224 | 14.4179
| 46 | 36.8 | 29.44 | 23.552 | 18.8416 | 15.0733
| 48 | 38.4 | 30.72 | 24.576 | 19.6608 | 15.7286
| 50 | 40 | 32 | 25.6 | 20.48 | 16.384
| 52 | 41.6 | 33.28 | 26.624 | 21.2992 | 17.0394
44m³/s | 0 | 1.1976 | 1.533 | 1.4716 | 1.2558 | 1.0046
46m³/s | 0 | 1.309 | 1.6755 | 1.6085 | 1.3726 | 1.098
48m³/s | 0 | 1.4253 | 1.8243 | 1.7514 | 1.4945 | 1.1956
50m³/s | 0 | 1.5465 | 1.9795 | 1.9004 | 1.6216 | 1.2973
52m³/s | 0 | 1.6727 | 2.1411 | 2.0554 | 1.754 | 1.4032
1,6m Pipe Diameter (in meters)
Pipe Diameter (in meters) | 1.6 | m
C = | 5.0265 | m
A = | 2.0106 | m²
Qty (m³/s) | 64 | 66 | 68 | 70 | 72 | m³/s
Fan Pressure | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | (Max x 0.85)
Duct Length m | 0 | 200 | 400 | 600 | 800 | 1000
Qty (m³/s) | 64 | 51.2 | 40.96 | 32.768 | 26.2144 | 20.9715
| 66 | 52.8 | 42.24 | 33.792 | 27.0336 | 21.6269
| 68 | 54.4 | 43.52 | 34.816 | 27.8528 | 22.2822
| 70 | 56 | 44.8 | 35.84 | 28.672 | 22.9376
| 72 | 57.6 | 46.08 | 36.864 | 29.4912 | 23.593
64m³/s | 0 | 1.2996 | 1.6635 | 1.597 | 1.3627 | 1.0902
66m³/s | 0 | 1.3821 | 1.7691 | 1.6983 | 1.4492 | 1.1594
68m³/s | 0 | 1.4671 | 1.8779 | 1.8028 | 1.5384 | 1.2307
70m³/s | 0 | 1.5547 | 1.99 | 1.9104 | 1.6302 | 1.3042
72m³/s | 0 | 1.6448 | 2.1054 | 2.0212 | 1.7247 | 1.3798
| Pipe Diameter (in meters) | 1.22 | m
| Qty (m³/s) | Duct Velocity - m/s | Speed = km/hr
| 45 | 38.4949 | 138.5816
| 42.75 | 36.5701 | 131.6525
| 40.6125 | 34.7416 | 125.0699
| 38.5819 | 33.0045 | 118.8164
| 36.6528 | 31.3543 | 112.8756
| 34.8201 | 29.7866 | 107.2318
| 33.0791 | 28.2973 | 101.8702
| 31.4252 | 26.8824 | 96.7767
| 29.8539 | 25.5383 | 91.9378
| 28.3612 | 24.2614 | 87.341
| 26.9432 | 23.0483 | 82.9739
| 25.596 | 21.8959 | 78.8252
| 24.3162 | 20.8011 | 74.8839
| 23.1004 | 19.761 | 71.1398
Note on C8: 10m is added to Fan length for intake distance piece and fan tail piece silencers etc.
Note on E12: Johan van Sittert: DO NOT CHANGE!!!
Note on C15: Johan van Sittert: Note: See guidelines for K-Factors table below
Note on C22: Johan van Sittert: DO NOT CHANGE!!!
Note on C23: Johan van Sittert: Change formula up to the fan pressure at distance required i.e. (Max distance of column to be installed)
Note on C26: * Remember to correct pressure for density = Pressure x density
Note on F57: Johan van Sittert: DO NOT CHANGE!!!
Note on E90: Johan van Sittert: DO NOT CHANGE!!!
Note on C91: Johan van Sittert: Note: See guidelines for K-Factors table

## Psychometry
[16 empty] | Cooler Duty 1 | [7 empty] | Back to INDEX | [26 empty] | Measured WB / DB |  |  |  |  | Simple Volume Calcs
W Hyg Correction
| 0.18032 |  | 0 | [14 empty] | Intake Conditions |  |  |  | Return Conditions | [10 empty] | Psycometric QTY - Masflow Calculator | [18 empty] | 0 | 0
[18 empty] | BP | WB Temp °C | DB Temp °C | Quantity | BP | WB Temp °C | DB Temp °C | Quantity | [7 empty] | Wet Bulb | Dry Bulb | BP | Qty | Massflow | Δ Volume m³/s | Δ MF kg/s | Remarks | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp) |  |  | Pt. | Wet Bulb | Dry Bulb | Pt. | Wet Bulb °C | Dry Bulb °C | BP kPa | Qty m³/s | Area | Velocity | Height | Width | Massflow kg/s | Δ Volume m³/s | Δ MF kg/s | Remarks | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp)
| 3.8895 |  | 2.063 | [14 empty] | 100 | 28.5 | 31.3 | 180 | 97.6 | 18 | 18 | 180 | [7 empty] | °C | °C | Kpa | m³/s | kg/s |  |  |  | Kpa | g/Kg | g/Kg | m³/Kg | Kg/m³ | Kj/Kg | Kj/Kg | % | °C |  |  | 1 | 20.3 | 29.3 | 1 | 20.3 | 29.3 | 111.7 | 39 | 26 | 1.5 | 1 | 26 | 49.8916 |  |  |  | 1.7335 | 0.009805 | 9.805 | 0.78936 | 1.2793 | 54.4859 | 53.6539 | 42.5534 | 15.262
[29 empty] | Pt 1 |  |  |  | 28.4 | 32 | 123.65 | 106.8 | 149.1388 | 106.8 | 149.1388 |  | 3.5803 | 0.018547 | 18.5471 | 0.72939 | 1.3964 | 79.6146 | 77.4128 | 75.3359 | 27.0797 |  |  | 2 | 20.5 | 29.5 | 2 | 20.5 | 29.5 | 111.6 | 149.52 | 26.7 | 5.6 | 1 | 26.7 | 190.9584 |  |  |  | 1.7636 | 0.0099873 | 9.9873 | 0.79082 | 1.2771 | 55.1562 | 54.3004 | 42.7974 | 15.5307
[29 empty] | Pt 2 |  |  |  | 26.5 | 26.5 | 123.65 | 216.3 | 307.7059 | 216.3 | 307.7059 |  | 3.4604 | 0.017908 | 17.908 | 0.71553 | 1.4226 | 72.2747 | 70.291 | 100 | 26.5 |  |  | 3 | 20.5 | 29.5 | 3 | 20.5 | 29.5 | 111.65 | 129.36 | 29.4 | 4.4 | 1 | 29.4 | 165.2859 |  |  |  | 1.7633 | 0.0099811 | 9.9811 | 0.79046 | 1.2777 | 55.1403 | 54.285 | 42.7904 | 15.5281
| 1.8517 |  | 1.2176 | [25 empty] | Pt 3 |  |  |  | 12.1 | 14.6 | 94.34 | 15 | 17.0488 | 15 | 17.0488 |  | 1.2593 | 0.0084148 | 8.4148 | 0.88723 | 1.1366 | 35.9396 | 35.514 | 75.8084 | 10.3835 |  |  | 4 | 20.5 | 29.5 | 4 | 20.5 | 29.5 | 110.5 | 31.185 | 34.65 | 0.9 | 5.5 | 6.3 | 39.4319 | 118.335 |  |  | 1.77 | 0.010125 | 10.1254 | 0.79886 | 1.2645 | 55.5089 | 54.6412 | 42.9522 | 15.587
| 3.8895 |  | 2.063 | [25 empty] | TOTAL |  |  |  | 22.3333 | 24.3667 | 113.88 | 338.1 | 473.8934 | 338.1 | 473.8934 |  | 2.5477 | 0.014234 | 14.2336 | 0.76696 | 1.3224 | 60.711 | 59.3822 | 83.5655 | 21.401 |  |  | 5 | 20.5 | 29.5 | 5 | 20.5 | 29.5 | 110.5 | 40.326 | 31.02 | 1.3 | 4.7 | 6.6 | 50.9903 |  |  |  | 1.77 | 0.010125 | 10.1254 | 0.79886 | 1.2645 | 55.5089 | 54.6412 | 42.9522 | 15.587
[52 empty] | 6 | 26.5 | 30.4 | 6 | 26.5 | 30.4 | 110.5 | 154.08 | 21.4 | 7.2 | 1 | 21.4 | 193.3045 | -113.754 |  |  | 3.1829 | 0.018447 | 18.4475 | 0.81179 | 1.2546 | 77.6986 | 75.6552 | 73.3501 | 25.088
Pw | 3.7091 | Pw | 2.063 | [48 empty] | 7 | 25 | 29.8 | 7 | 25 | 29.8 | 110.6 | 111.36 | 19.2 | 5.8 | 1 | 19.2 | 140.2875 |  |  |  | 2.8243 | 0.0163 | 16.2999 | 0.80674 | 1.2598 | 71.5895 | 69.8861 | 67.3652 | 23.0956
[17 empty] | Intake Conditions |  |  |  | Return Conditions | [7 empty] | Main Fan (Total Press: 1234Pa) |  |  |  | 16.4 | 17.3 | 91.94 | 350.2 | 383.373 |  |  |  | 1.8111 | 0.012499 | 12.4985 | 0.92489 | 1.0947 | 49.0346 | 48.1778 | 91.7501 | 10.1618 |  |  | 8 | 24.4 | 29.3 | 8 | 24.4 | 29.3 | 110.5 | 61.732 | 10.12 | 6.1 | 2.2 | 4.6 | 77.8571 |  |  |  | 2.7061 | 0.015615 | 15.615 | 0.80527 | 1.2612 | 69.3232 | 67.7306 | 66.4298 | 22.3901
[30 empty] | Measured WB / DB | [21 empty] | 9 | 27.3 | 31.1 | 9 | 27.3 | 31.1 | 110.3 | 202.52 | 33.2 | 6.1 | 1 | 33.2 | 252.875 |  |  |  | 3.3569 | 0.019524 | 19.5241 | 0.81651 | 1.2486 | 81.1783 | 78.9503 | 74.3325 | 25.9853
r | 0.02396 | r | 0.013431 | [13 empty] | Vapour Pressure | Pw | 3.7091 | kPa | Vapour Pressure | Pw | 2.063 | kPa | [5 empty] | W Hyg Correction | [21 empty] | 10 | 25 | 27.2 | 10 | 25 | 27.2 | 109.4 | 322.04 | 33.2 | 9.7 | 1 | 33.2 | 404.4598 |  |  |  | 3.0112 | 0.017605 | 17.6051 | 0.81024 | 1.2559 | 72.2282 | 70.3885 | 83.5148 | 24.1601
[30 empty] | 0.5 | 0.8 | [20 empty] | 11 | 29.5 | 30.8 | 11 | 29.5 | 30.8 | 109.4 | 402.21 | 32.7 | 12.3 | 1 | 32.7 | 497.3904 |  |  |  | 4.0293 | 0.023785 | 23.7847 | 0.82787 | 1.2366 | 91.758 | 88.8252 | 90.7594 | 29.1102
[17 empty] | Moisture Content | r | 23.9596 | g/kg | Moisture Content | r | 13.4311 | g/kg | [5 empty] | Wet Bulb | Dry Bulb | Pt. | Wet Bulb °C | Dry Bulb °C | BP kPa | Qty m³/s | Massflow kg/s | Δ Volume m³/s | Δ MF kg/s | Remarks | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp) |  |  | 12 | 27.3 | 29.8 | 12 | 27.3 | 29.8 | 109.4 | 399.135 | 32.45 | 12.3 | 5.9 | 5.5 | 496.221 |  |  |  | 3.4507 | 0.020258 | 20.2579 | 0.82064 | 1.2432 | 81.7006 | 79.3889 | 82.3041 | 26.4522
[30 empty] | 27 | 32 | 1 | 28.4 | 32 | 123.65 | 30.6 | 42.7308 | 30.6 | 42.7308 |  | 3.5803 | 0.018547 | 18.5471 | 0.72939 | 1.3964 | 79.6146 | 77.4128 | 75.3359 | 27.0797 |  |  | 13 | 22.8 | 24.5 | 13 | 22.8 | 24.5 | 109.4 | 405.06 | 31.4 | 12.9 | 1 | 31.4 | 513.9812 |  |  |  | 2.6545 | 0.015468 | 15.4676 | 0.80027 | 1.2689 | 63.9891 | 62.515 | 86.3774 | 22.0735
asv | 0.90743 | asv | 0.87464 | [13 empty] | Specific Volume | asv | 0.90743 | m3/kg | Specific Volume | asv | 0.87464 | m3/kg | [5 empty] | 26.5 | 30 | 2 | 27 | 30.8 | 97.95 | 200.4 | 222.1321 | 65.3 | 222.1321 |  | 3.3239 | 0.021849 | 21.8487 | 0.92188 | 1.1084 | 86.8089 | 84.343 | 74.8706 | 25.8184 |  |  | 14 | [11 empty] | 0 |  |  | DT Passing | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[30 empty] | 26.3 | 29.3 | 3 | 26.8 | 30.1 | 97.95 | 169.5 | 188.3223 | 65.3 | 72.781 |  | 3.3138 | 0.02178 | 21.7802 | 0.91966 | 1.111 | 85.903 | 83.463 | 77.6914 | 25.7672 |  |  | 15 |  |  | 15 | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[17 empty] | Density | w | 1.1284 | kg/m3 | Density | w | 1.1587 | kg/m3 | [5 empty] | 26.3 | 29 | 4 | 26.8 | 29.8 | 97.67 | 104.2 | 115.5412 | 380.1 | 419.6523 |  | 3.3333 | 0.021978 | 21.9777 | 0.92166 | 1.1088 | 86.0942 | 83.6322 | 79.5047 | 25.8661 |  |  | 16 |  |  | 16 | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[30 empty] | 26 | 28.5 | 5 | 26.5 | 29.3 | 97.98 | 131.2 | 146.2173 | 131.2 | 146.2173 |  | 3.2837 | 0.021569 | 21.5686 | 0.91665 | 1.1145 | 84.527 | 82.1379 | 80.6085 | 25.6131 |  |  | 17 |  |  | 17 | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
w | 1.1284 | w | 1.1587 | [13 empty] | Enthalpy | H | 92.7293 | kJ/kg | Enthalpy | H | 52.1164 | kJ/kg | [5 empty] | 28.8 | 31.3 | 6 | 29.3 | 32.1 | 97.98 | 238.5 | 262.7298 | 275.9 | 304.1111 |  | 3.897 | 0.025764 | 25.7636 | 0.93116 | 1.1016 | 98.1838 | 95.0285 | 81.5375 | 28.5332 |  |  | 18 |  |  | 18 | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[30 empty] | 27.8 | 31.3 | 7 | 28.3 | 32.1 | 97.98 | 156.2 | 172.2657 | 248.9 | 273.435 |  | 3.6048 | 0.023758 | 23.7582 | 0.92828 | 1.1029 | 93.0524 | 90.242 | 75.4242 | 27.1961 |  |  | 19 |  |  | 19 | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[17 empty] | Sigma Heat | S | 89.875 | kJ/kg | Sigma Heat | S | 51.1059 | kJ/kg | [5 empty] | 29.8 | 34 | 8 | 30.3 | 34.8 | 97.98 | 92.7 | 101.1693 |  |  |  | 4.0306 | 0.026685 | 26.6846 | 0.94074 | 1.0914 | 103.3838 | 100.0041 | 72.5169 | 29.1157 |  |  | 20 |  |  | 20 | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[30 empty] | 30 | 34 | 9 | 30.5 | 34.8 | 97.98 | 120.8 | 131.8045 |  |  |  | 4.0928 | 0.027115 | 27.1147 | 0.94136 | 1.0911 | 104.4864 | 101.0296 | 73.6369 | 29.3814
H | 92.7293 | H | 52.1164 | [13 empty] | Massflow | M | 203.1152 | kg/s | Massflow | M | 205.8001 | kg/s | [5 empty] | 26.3 | 30 | 10 | 26.8 | 30.8 | 97.98 | 103.2 | 114.4511 | 24.9 | 27.1794 |  | 3.2696 | 0.021473 | 21.4727 | 0.92106 | 1.109 | 85.8476 | 83.4422 | 73.6476 | 25.5405 |  |  | Round
[30 empty] | 26.3 | 30 | 11 | 26.8 | 30.8 | 97.98 | 92.1 | 102.141 | 11.1 | 12.3102 |  | 3.2696 | 0.021473 | 21.4727 | 0.92106 | 1.109 | 85.8476 | 83.4422 | 73.6476 | 25.5405 |  | Measured WB / DB
[17 empty] | Relative Humidity |  | 81.2047 | % | Relative Humidity |  | 100 | % | [5 empty] | 28.3 | 33.8 | 12 | 28.8 | 34.6 | 97.98 | 21.5 | 23.5199 | 70.6 | 78.6211 |  | 3.5917 | 0.023669 | 23.6685 | 0.93575 | 1.094 | 95.4421 | 92.5928 | 65.3408 | 27.134 |  |  | W Hyg Correction
[30 empty] | 29.5 | 34.3 | 13 | 30 | 35.1 | 97.98 | 116.7 | 127.2936 | 25.6 | 28.0308 |  | 3.9192 | 0.025916 | 25.9165 | 0.94054 | 1.0908 | 101.7301 | 98.4801 | 69.353 | 28.6312 |  |  | Pt. | Wet Bulb | Dry Bulb | Pt. | Wet Bulb °C | Dry Bulb °C | BP kPa | Qty m³/s | Area | Velocity | Diameter | Massflow kg/s | Δ Volume m³/s | Δ MF kg/s | Remarks |  | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp)
S | 89.875 | S | 51.1059 | [13 empty] | Dewpoint Temp °C. | tdp | 27.6842 | 0C | Dewpoint Temp °C. | tdp | 18 | 0C | [5 empty] | 29.5 | 34 | 14 | 30 | 34.8 | 97.98 | 51.7 | 56.4439 | 65 | 70.8497 |  | 3.9381 | 0.026047 | 26.0469 | 0.93981 | 1.0918 | 101.7489 | 98.4826 | 70.8535 | 28.7144 |  |  | 1 | 25 | 27.2 | 1 | 25 | 27.2 | 97 | 172.7876 | 19.635 | 8.8 | 5 | 192.1402 |  |  |  |  | 3.0288 | 0.020048 | 20.0477 | 0.91731 | 1.112 | 78.4569 | 76.3619 | 84.0021 | 24.2571
[30 empty] | 31.5 | 35 | 15 | 32 | 35.8 | 97.98 | 26.7 | 28.9902 | 25 | 27.4537 |  | 4.5127 | 0.030031 | 30.0306 | 0.94866 | 1.0858 | 113.0206 | 109.0037 | 76.8345 | 31.087 |  |  | 2 |  |  | 2 | 25.5 | 28 |  | 0 | 0 |  |  | 0 |  |  |  |  | 3.2618 | -0.622 | -622 | -26.498 | -0.014265 | -1558.8308 | -1492.5318 | 86.3338 | 25.5
[30 empty] | 24.5 | 27.8 | 16 | 25 | 28.6 | 97.98 | 42.3 | 47.3147 |  |  |  | 2.9391 | 0.019235 | 19.2349 | 0.91121 | 1.1186 | 77.8396 | 75.8295 | 75.1278 | 23.7561 |  |  | 3 |  |  | 3 | 25.5 | 28 |  | 0 | 0 |  |  | 0 |  |  |  |  | 3.2618 | -0.622 | -622 | -26.498 | -0.014265 | -1558.8308 | -1492.5318 | 86.3338 | 25.5
[17 empty] | BP = 87.5 | ξH | kg/s | Heat | [9 empty] | 25.8 | 29 | 17 | 26.3 | 29.8 | 97.98 | 82 | 91.2652 | 82 | 91.2652 |  | 3.199 | 0.020993 | 20.9933 | 0.91734 | 1.113 | 83.5794 | 81.2715 | 76.3013 | 25.173 |  |  | 4 |  |  | 4 | 25.5 | 28 |  | 0 | 0 |  |  | 0 |  |  |  |  | 3.2618 | -0.622 | -622 | -26.498 | -0.014265 | -1558.8308 | -1492.5318 | 86.3338 | 25.5
| 96.3372 |  | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | Content | [9 empty] | 25.8 | 29.8 | 18 | 26.3 | 30.6 | 97.98 | 47.7 | 52.9603 | 49.2 | 54.9521 |  | 3.1485 | 0.020651 | 20.6511 | 0.91928 | 1.1103 | 83.5388 | 81.2685 | 71.7341 | 24.9058 |  |  | 5 |  |  | 5 | 25.5 | 28 |  | 0 | 0 |  |  | 0 |  |  |  |  | 3.2618 | -0.622 | -622 | -26.498 | -0.014265 | -1558.8308 | -1492.5318 | 86.3338 | 25.5
|  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | ξH at 7.0/7.0 | 25.03 | 750 | 18772.5 | [9 empty] | 25.8 | 28.5 | 19 | 26.3 | 29.3 | 97.98 | 18.7 | 20.8448 | 82 | 91.2652 |  | 3.2305 | 0.021207 | 21.2074 | 0.91613 | 1.1147 | 83.6048 | 81.2734 | 79.3033 | 25.338 |  |  | 6 |  |  | 6 | 25.5 | 28 |  | 0 | 0 |  |  | 0 |  |  |  |  | 3.2618 | -0.622 | -622 | -26.498 | -0.014265 | -1558.8308 | -1492.5318 | 86.3338 | 25.5
| 4.5676 |  | 2.063 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | ξH at 18.0/30 | 55.2 | 50 | 2760 | [9 empty] | 25.2 | 28 | 20 | 25.7 | 28.8 | 97.98 | 81.2 | 90.7074 | 34.3 | 38.305 |  | 3.1051 | 0.020357 | 20.3568 | 0.91341 | 1.1171 | 80.9115 | 78.7247 | 78.4567 | 24.6729 |  |  | 7 |  |  | 7 | 25.5 | 28 |  | 0 | 0 |  |  | 0 |  |  |  |  | 3.2618 | -0.622 | -622 | -26.498 | -0.014265 | -1558.8308 | -1492.5318 | 86.3338 | 25.5
|  |  |  | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 | 1.6931 |  | Total kg/s |  | 800 | 26.9156 | ξH (S) | [8 empty] | 25.2 | 28 | 21 | 25.7 | 28.8 | 97.98 | 81.2 | 90.7074 | 29 | 32.1155 |  | 3.1051 | 0.020357 | 20.3568 | 0.91341 | 1.1171 | 80.9115 | 78.7247 | 78.4567 | 24.6729 |  |  | 8 |  |  | 8 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
| 81.2047 |  | 100 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 | 0.010713 |  |  |  |  | 28.5 | °C WB | [8 empty] | 25.2 | 28 | 22 | 25.7 | 28.8 | 97.98 | 81.2 | 90.7074 | -62.5 | -69.8626 |  | 3.1051 | 0.020357 | 20.3568 | 0.91341 | 1.1171 | 80.9115 | 78.7247 | 78.4567 | 24.6729 |  |  | 9 |  |  | 9 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
| 3.0056 |  | 0 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | 0.88503 | [14 empty] | 25.2 | 28 | 23 | 25.7 | 28.8 | 97.98 | 81.2 | 90.7074 | 0 | 0 |  | 3.1051 | 0.020357 | 20.3568 | 0.91341 | 1.1171 | 80.9115 | 78.7247 | 78.4567 | 24.6729 |  |  | 10 |  |  | 10 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
| 12.3307 |  | 0.6105 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | 1.142 | [14 empty] | 25.2 | 28 | 24 | 25.7 | 28.8 | 97.98 | 81.2 | 90.7074 | 0 | 0 |  | 3.1051 | 0.020357 | 20.3568 | 0.91341 | 1.1171 | 80.9115 | 78.7247 | 78.4567 | 24.6729 |  |  | 11 |  |  | 11 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[17 empty] | Duty (kW) | 7874.6054 | Kj/s | [10 empty] | 25.2 | 28 | 25 | 25.7 | 28.8 | 97.98 | 81.2 | 90.7074 | 0 | 0 |  | 3.1051 | 0.020357 | 20.3568 | 0.91341 | 1.1171 | 80.9115 | 78.7247 | 78.4567 | 24.6729 |  |  | 12 |  |  | 12 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
Pw | -84.0065 | Pw | 0.6105 | [48 empty] | 13 |  |  | 13 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[52 empty] | 14 |  |  | 14 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[52 empty] | 15 |  |  | 15 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
| 1.8043 |  | 1.2176 | [48 empty] | 16 |  |  | 16 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[52 empty] | 17 |  |  | 17 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
tdp | 27.6842 | tdp | 18 | [12 empty] | Cooler Duty 2 | [8 empty] | Back to INDEX |  |  |  | Barrometric pressure calculator |  |  |  |  | 9.79 | m/s2 | [6 empty] | Refrigeration expressed as tonnes | [9 empty] | 18 |  |  | 18 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[34 empty] | 0.02897 | kg/mol | [16 empty] | 19 |  |  | 19 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[29 empty] | BP |  |  | Mean Sea Level BP kPa |  | 8.3158 | J/(mol·K) | [6 empty] | Tons Refrigeration |  | 5000 | tons | [6 empty] | 20 |  |  | 20 | 0 | 0 |  | 0 | 0 |  |  | 0 |  |  |  |  | 0.6105 | -0.622 | -622 | -128.4096 | -0.0029437 | -1555.622 | -1555.622 | 100 | 0
[24 empty] | Surface BP Kpa |  |  |  |  | kPa |  |  |  | Shaft Collar above sea level |  | 717 | [6 empty] | Factor |  | 3.51
[17 empty] | Air In | [6 empty] | 82.3 | Level | Depth below surface | BP (kPa) Calculated |  | BP (kPa) Calculated - Old Formula |  |  | 101.325 | Level | Depth below surface | BP (kPa) Calculated | Old Formula kPa | Shaft Collar + level above sea level |  |  |  |  | kW Refrigeration |  | 17550 | kW
[17 empty] | Wet Bulb Temp °C | 25 | °C |  | Duty Calculation |  |  |  | 44 | -1885 | 100.7541 | kPa | 94.3056 |  |  | Shaft Collar |  | 0 | BP 93,1 kPa |  | 717
[17 empty] | Dry Bulb Temp °C | 35 | °C |  | Sigma Heat IN | 81.0844 | Kj/Kg |  | 47 | -800 | 90.132 | kPa | First Level depth below collar |  |  | -940 | 1 | -940 | BP 104 kPa | 103.5082 | -223
[17 empty] | BP | 89 | Kpa |  | Sigma Heat OUT | 75.6958 | Kj/Kg |  | 50 | -1000 | 92.09 | kPa | Level Spacing in meters |  |  | -60 | 2 | -1000 | BP 104,8 kPa | 104.0956 | -283
[17 empty] | Density ( w ) | 0.99526 | Kg/m³ |  | Density Air In | 0.99526 | Kg/m³ |  | 53 | -1590 | 97.8661 | kPa |  |  |  |  | 3 | -1060 | BP 105,5 kPa | 104.683 | -343
[17 empty] | Vapour Press (Pw) | 2.5931 | Kpa |  | Quantity of Air | 262 | m³/s |  | 56 | -1680 | 98.7472 | kPa |  |  |  |  | 4 | -1120 | BP 106,3 kPa | 105.2704 | -403
[17 empty] | Moisture Content ( r ) | 0.018666 | g/Kg |  | DUTY (KW) | 1405.1251 | Kj/s |  | 59 | -1770 | 99.6283 | kPa |  |  |  |  | 5 | -1180 | BP 107 kPa | 105.8578 | -463
[17 empty] | Moisture Content ( g/Kg ) | 18.6661 | g/Kg |  | Massflow (kg/s) | 260.758 | Kg/s |  | 62 | -1860 | 100.5094 | kPa |  |  |  |  | 6 | -1240 | BP 107,8 kPa | 106.4452 | -523
[17 empty] | Specific Volume ( v ) | 1.0235 | m³/Kg | [5 empty] | 64 | -1950 | 101.3905 | kPa |  |  |  |  | 7 | -1300 | BP 108,6 kPa | 107.0326 | -583
[17 empty] | Enthalpy ( H ) | 83.035 | Kj/Kg | [5 empty] | 68 | -2040 | 102.2716 | kPa |  |  |  |  | 8 | -1360 | BP 109,3 kPa | 107.62 | -643
[17 empty] | Sigma Heat ( S ) | 81.0844 | Kj/Kg |  | Fan (KW) If applicable | 0 | Kj/s |  | 70 | -2130 | 103.1527 | kPa |  |  |  |  | 9 | -1420 | BP 110,1 kPa | 108.2074 | -703
[17 empty] | Relative Humidity | 46.1406 | % |  | TOTAL Duty (KW) | 1405.1251 | Kj/s |  | 73 | -2220 | 104.0338 | kPa |  |  |  |  | 10 | -1480 | BP 110,9 kPa | 108.7948 | -763
[17 empty] | Dewpoint Temp °C (tdp ) | 21.6897 | °C | [5 empty] | 76 | -2310 | 104.9149 | kPa |  |  |  |  | 11 | -1540 | BP 111,7 kPa | 109.3822 | -823
[25 empty] | 85 | -2604 | 107.7932 | kPa |  |  |  |  | 12 | -1600 | BP 112,5 kPa | 109.9696 | -883
[17 empty] | Simple Density ( w ) 1 / ASV | 0.97702 | Kg/m³ |  | Liters @ UC # | 4.8673 | L/Sec |  | 88 | -2699 | 108.7232 | kPa |  |  |  |  | 13 | -1660 | BP 113,3 kPa | 110.557 | -943
[25 empty] | 92 | -2798 | 109.6924 | kPa |  |  |  |  | 14 | -1720 | BP 114,1 kPa | 111.1444 | -1003
[17 empty] | 1900-01-25 | [7 empty] | 95 | -2904 | 110.7302 | kPa |  |  |  |  | 15 | -1780 | BP 114,9 kPa | 111.7318 | -1063
[17 empty] | Wet Bulb Temp °C | 27 | °C |  | Design Δt Over Cooler | 14 | °C |  | 98 | -2974 | 111.4155 | kPa | Note: |  |  | BAROMETRIC PRESSURE INCREASE OR DECEASE
[17 empty] | Dry Bulb Temp °C | 35 | °C |  | Cooler L/Sec Req. | 23.9709 | l/s |  | 99 | -3013 | 111.7973 | kPa | The approximate barometric pressure increase or decease in a vertical shaft = 1 kPa/100m
[17 empty] | BP | 114.8 | Kpa | [5 empty] | 101 | -3052 | 112.1791 | kPa | The Substitute climate temperature [tzk] is determined from wet and dry bulb temperature as well as air velocity using the following formula:
[17 empty] | Vapour Press (Pw) | 2.9721 | Kpa |  | Reduction of DB Temperatures |  |  |  | 102 | -3091 | 112.5609 | kPa | tzk=0.6•tw+0.4•ts-v
[17 empty] | Moisture Content ( r ) | 0.016531 | r |  | Air in Moisture Content ( g/Kg ) | 10.294 | g/kg |  | 103 | -3130 | 112.9427 | kPa | where:
[17 empty] | Moisture Content ( g/Kg ) | 16.5314 | g/Kg |  | Fan Massflow (kg/s) | 34.5 | kg/s |  | 105 | -3211 | 113.7357 | kPa | tzk - substitute climate temperature [°C],
[17 empty] | Specific Volume ( v ) | 0.79085 | m³/Kg |  | Air out Moisture Content ( g/Kg ) | 15.452 | g/kg |  | 106 | -3253 | 114.1469 | kPa | tw – wet bulb temperature [°C],
[17 empty] | Density ( w ) | 1.2854 | Kg/m³ |  | Delta Moisture Content ( g/Kg ) | 5.158 | g/kg |  | 108 | -3295 | 114.558 | kPa | ts – dry bulb temperature [°C],
[17 empty] | Enthalpy ( H ) | 77.5615 | Kj/Kg |  | Water Requirement (g/s) | 177.951 | g/s |  | 111 | -3372 | 115.3119 | kPa | v – air velocity [m/s] multiplied by re-calculating coefficient [1s •°C/m]
[17 empty] | Sigma Heat ( S ) | 75.6958 | Kj/Kg |  | Water Requirement (l/s) | 0.17795 | l/s |  | 114 | -3457 | 116.144 | kPa
[17 empty] | Relative Humidity | 52.8858 | % |  | Water Requirement (l/Hr) | 640.6236 | l/Hr |  | 115 | -3499 | 116.5552 | kPa | Permissible boundary values of equivalent temperature of climate are as follows:
[17 empty] | Dewpoint Temp °C (tdp ) | 23.9423 | °C | [9 empty] | · For light work tzk <30 °C
[21 empty] | 1503.3 | 1748.8367 | [6 empty] | · For moderate work tzk <28 °C
· For hard work tzk <25 °C
[17 empty] | Calculate Qty From MF | [11 empty] | · For the above ranges work time should be shortened if tzk is greater than boundary values
[17 empty] | Airflow |  |  |  | 22.8 | 27.1 | 10.1 | 37.25 | 376.225 | 423.7364 | 1.1263 | 98 | · Work not allowed when tzk > 32 °C
[17 empty] | Massflow given | 91.1 | Kg/s
[17 empty] | Qty = | 91.5339 | m³/s | [9 empty] | tw | 27.5 | °C Wb | [22 empty] | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp)
[29 empty] | ts | 29 | °C Db | [12 empty] | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp)
[29 empty] | v | 0.5 | m/s
[29 empty] | TZK = | 27.6 | °C
Back to INDEX
[16 empty] | 2026-03-05 09:19 | Survey Frequency : |  | 90 |  | Days | [22 empty] | Air IN | [8 empty] | Air OUT
[16 empty] | Next Due Date | CAR NR | FAN NR | Format : yyyy/mm/dd i.e.: 2015/05/19 | Days Overdue | LEV | WORKPLACE | OE Officer Respponsible | Air In |  | BP | Air Out |  | BP | Volume m³/s | Massflow kg/s | Air Duty kW | Water Duty kW | Water in | Water Out | Actual Flow | Calculated Water flow | Eff % | Remarks |  |  |  |  | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp) | Vapour Press (Pw) | Moisture Content (r) | Moisture Content (g/Kg) | Specific Volume (v) | Density (w) | Enthalpy (H) | Sigma Heat (S) | Relative Humidity (rh) | Dewpoint Temp °C temperature (tdp)
[24 empty] | W/B Temp °C | D/B Temp °C | kPa | W/B Temp °C | D/B Temp °C | kPa | [7 empty] | Water flow
85 level
[16 empty] | 2025-08-17 | XXXX | xx-1111 | 2025-05-19 | 200.3884 | xx | EAST XX CONN X/C | Mr X. Xxxxx | 28.4 | 32 | 123.65 | 26.5 | 26.5 | 123.65 | 8.7 | 12.1489 | 86.5225 | 128.1222 | 22.3 | 25.9 | 8.5 | 5.7402 | 59.0164 | [5 empty] | 3.5803 | 0.018547 | 18.5471 | 0.72939 | 1.3964 | 79.6146 | 77.4128 | 75.3359 | 27.0797 | 3.4604 | 0.017908 | 17.908 | 0.71553 | 1.4226 | 72.2747 | 70.291 | 100 | 26.5
[16 empty] | Water Flow "Back Calc" - Coolers | [7 empty] | Note: To convert 1 g of ice at 0 ºC to 1 g of water at 0 ºC, 334 J of heat ... remains the same only and that is why there is no temperature change (DT)
The specific heat capacity, or the amount of heat needed to raise the temperature of a specific substance in a specific form one degree Celsius, for water is 4.187 kJ/kgK, for ice 2.108 kJ/kgK, and for water vapor (steam) 1.996 kJ/kgK.
[17 empty] | Air Duty kW | 14805 | kW | Water - Δ t
[17 empty] | Water Temp °C in | 10.2 | °C | 11.8 | °C
[17 empty] | Water Temp °C Out | 22 | °C
[17 empty] | Estimated Coil / BAC Efficiency | 85
[17 empty] | Calculated Water flow | 299.6563 | l/s
[17 empty] | Calculated Water flow - Eff% | 344.6048 | l/s
Cooling Coil / Heat Exchanger Water Duty Calc
WATER Duty Calc
[17 empty] | Water Temperature IN | 18.6 | °C
[17 empty] | Water Temperature OUT | 22 | °C
[17 empty] | Water Flow | 344.6048 | l/s
[17 empty] | Water specific heat capacity | 4.187 | kJ/kgK
[17 empty] | Water DUTY (kW) | -4905.7246 | KW |  | -4169.8659
[16 empty] | Density ( w ) - [Single Calc] - Vertical data |  |  |  |  | Density ( w ) - [Single Calc] - Horizontal data
Relative Humidity Calc (Single Formulae)
[17 empty] | Wet Bulb Temp °C | 26.5 | °C |  | Wet Bulb Temp °C | Dry Bulb Temp °C | BP | Density ( w ) - [Single Calc]
[17 empty] | Dry Bulb Temp °C | 30.8 | °C |  | 19 | 20.5 | 81.98 | 0.96324
[17 empty] | BP | 98.55 | Kpa |  | Relative Humidity | 87.8307 | %
[17 empty] | Relative Humidity | 71.798 | % |  |  | Single Calc Humidity
[17 empty] | Density ( w ) - [Single Calc] | 1.1159 | Kg/m³
Formulas:
Cooler Duty 1 = IF(ISBLANK([WB Temp °C]),"",([WB Temp °C]+V90))
Note on AK47: Earth-surface gravitational acceleration
Note on AK48: Molar mass of dry air
Note on AK49: Universal gas constant
Note on AI51: DO NOT CHANGE Sea level standard atmospheric pressure
Note on AB52: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC52: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB53: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC53: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AI53: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB54: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC54: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB55: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC55: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB56: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC56: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB57: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC57: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB58: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC58: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB59: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC59: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB60: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC60: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on Y61: NOTE!!! 100% of fan Kw is added as heat (Only add this if Intake temperature is measured BEFORE THE FAN/S!!!)
Note on AB61: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC61: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB62: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC62: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB63: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC63: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB64: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC64: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB65: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC65: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB66: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC66: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB67: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC67: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB68: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC68: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB69: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC69: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB70: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC70: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB71: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC71: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB72: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC72: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB73: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC73: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB74: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC74: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB75: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC75: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB76: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC76: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB77: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC77: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on AB78: Johan van Sittert: You can enter any applicable value for level you require here
Note on AC78: Johan van Sittert: You can enter any applicable value for level you require here (Remember "-" going down
Note on T82: Johan van Sittert: Note: enter BP, WB and DB at "Air In" - ABOVE
Note on U84: Johan van Sittert: Note: enter BP, WB and DB at "Air In" - ABOVE
Note on V94: NOTE: Date FORMAT

## Thermal Stress
Back to INDEX
WBGT calculator (Shade) |  | The WBGT is calculated for surface indoor exposure, or outdoor exposure with no solar load (i.e. measured outdoor in shade) |  |  |  | The Substitute climate temperature [tzk] is determined from wet and dry bulb temperature as well as air velocity using the following formula:
tzk=0.6•tw+0.4•ts-v
WBGT = 0,7 tnwb + 0,3 tg | [5 empty] | where:
where: | tnwb = Mean Wetbulb Temperature |  |  |  |  | tzk - substitute climate temperature [°C],
| tg= Mean Drybulb Temperature |  |  |  |  | tw – wet bulb temperature [°C],
ts – dry bulb temperature [°C],
Mean Wetbulb Temperature |  | 25 | °C Wb |  |  | v – air velocity [m/s] multiplied by re-calculating coefficient [1s •°C/m]
Mean Globe-Temp |  | 37 | °C tg
WBGT = |  | 28.6 | °C |  |  | Permissible boundary values of equivalent temperature of climate are as follows:
· For light work tzk <30 °C
· For moderate work tzk <28 °C
WBGT calculator (Sunlight) |  | For outdoors sunlight exposure |  |  |  | · For hard work tzk <25 °C
WBGT = 0.7 T nwb + 0.2 T g + 0.1 T a | [5 empty] | · For the above ranges work time should be shortened if tzk is greater than boundary values
where: | tnwb = Mean Wetbulb Temperature |  |  |  |  | · Work not allowed when tzk > 32 °C
tg = Mean globe temperature
| ta= Mean Drybulb Temperature |  |  |  |  | tw | 27.5 | °C Wb
Mean Wetbulb Temperature |  | 25 | °C Wb |  |  | ts | 29 | °C Db
Mean Globe-Temp |  | 37 | °C tg |  |  | v | 0.5 | m/s
Mean Drybulb Temperature |  | 35 | °C Db |  |  | TZK = | 27.6 | °C
WBGT = |  | 28.4 | °C
BMI Calculator
BMI = body mass (kg) / height (m)2 |  |  | Body Mass Indicator | < 15 : emaciated
where: | B = body mass measured in kilogram |  |  | 15 - 19 : underweight
| Length = Person's Length measured in Meter |  |  | 20 - 25 : normal body fat content
26 - 29 : overweight (warning)
Body mass |  | 97 | kg | 30 - 35 : obese (overt risk factor)
Height |  | 1.73 | m | > 35 : exclusion
BMI = |  | 32.41 | °C
DI Calculator |  |  | "Israeli Discomfort Index (DI)"
DI =Discomfort Index |  |  |  | DI < 22: No heat load; no action required
where: | WB = Wetbulb Temperature |  |  | DI 22 – 24: Mild; slight discomfort, no action required
| DB = Drybulb Temperature |  |  | DI 24 – 28: Moderate; unspecified rest periods and water breaks every hour
DI > 28: Severe; heavy work requires a 30/15-minute work-rest regimen and drinking large amounts of cold beverage.
Wetbulb Temperature |  | 22 | °C Wb
Drybulb Temperature |  | 31 | °C Db
DI = |  | 26.5 | °C
Note on B9: measured with a globe thermometer, also known as a black globe thermometer
Note on B19: measured with a globe thermometer, also known as a black globe thermometer

## Refrigeration
Back to INDEX
Refrigeration Plant Survey
| EVAPORATOR | Plant 1 |  | Plant 2 |  | Plant 3
| Temperature Refigerant IN | 3.3 | °C | 3.4 | °C | 3.4 | °C
| Temperature Refigerant OUT | 15.3 | °C | 15.5 | °C | 15.4 | °C
| Refrigerant Flow | 123.5 | l/s | 122.8 | l/s | 122.8 | l/s
| EVAPORATOR DUTY (kW) | 1482 | KW | 1485.88 | KW | 1473.6 | KW
CONDENSER
| Temperature Refigerant IN | 45.3 | °C | 45.1 | °C | 45 | °C
| Temperature Refigerant OUT | 25.3 | °C | 25 | °C | 25.1 | °C
| Refrigerant Flow | 80.2 | l/s | 123.1 | l/s | 123 | l/s
| CONDENSER DUTY (kW) | 1604 | KW | 2474.31 | KW | 2447.7 | KW
| TOTAL EVAPORATOR DUTY | 4441.48
| TOTAL CONDENSER DUTY | 6526.01
Compressor motor input power
| E = voltage [kV] | 6.6 | kV | 6.6 | kV | 6.6 | kV
| I = current [amperes] | 150 | A | 240 | A | 240 | A
| pf = power factor [normally approximately 0.9] | 0.9 | pf | 0.9 | pf | 0.9 | pf
| n = number of phases [normally 3] | 3 | n | 3 | n | 3 | n
| W = Electric power [kW] | 1543.2573 | kW | 2469.2116 | kW | 2469.2116 | kW
| Percentage error:- | -88.6071 | % | -59.8462 | % | -61.0823 | %
| Condenser Tower (WATER) |  |  |  | Pre Cooling Tower (WATER) |  |  |  | Surface BAC (WATER)
| Water Temperature IN | 41 | °C |  | Water Temperature IN |  | 23.5 | °C | Water Temperature IN | 23.5 | °C
| Water Temperature OUT | 25.8 | °C |  | Water Temperature OUT |  | 19.3 | °C | Water Temperature OUT | 19.3 | °C
| Water Flow | 100 | l/s |  | Water Flow |  | 235 | l/s | Water Flow | 235 | l/s
| Water specific heat capacity | 4.187 | kJ/kgK |  | Water specific heat capacity |  | 4.187 | kJ/kgK | Water specific heat capacity | 4.187 | kJ/kgK
| Condenser Cooling Tower DUTY (kW) | 6364.24 | KW |  | Pre Cooling Tower DUTY (kW) |  | 4132.569 | KW | BAC DUTY (kW) | 4132.569 | KW
| Condenser Tower Ambient Air In |  |  |  | Pre Cooling Tower Ambient Air In |  |  |  | BAC Tower Ambient Air In
| Wet Bulb Temp °C | 18 | °C |  | Wet Bulb Temp °C |  | 18 | °C | Wet Bulb Temp °C | 18 | °C
| Dry Bulb Temp °C | 35 | °C |  | Dry Bulb Temp °C |  | 35 | °C | Dry Bulb Temp °C | 35 | °C
| BP | 91.1 | Kpa |  | BP |  | 91.1 | Kpa | BP | 91.1 | Kpa
| Density ( w ) | 1.0255 | Kg/m³ |  | Density ( w ) |  | 1.0255 | Kg/m³ | Density ( w ) | 1.0255 | Kg/m³
| Vapour Press (Pw) | 1.0656 | Kpa |  | Vapour Press (Pw) |  | 1.0656 | Kpa | Vapour Press (Pw) | 1.0656 | Kpa
| Moisture Content ( r ) | 0.0073618 | g/Kg |  | Moisture Content ( r ) |  | 0.0073618 | g/Kg | Moisture Content ( r ) | 0.0073618 | g/Kg
| Moisture Content ( g/Kg ) | 7.3618 | g/Kg |  | Moisture Content ( g/Kg ) |  | 7.3618 | g/Kg | Moisture Content ( g/Kg ) | 7.3618 | g/Kg
| Specific Volume ( v ) | 0.98228 | m³/Kg |  | Specific Volume ( v ) |  | 0.98228 | m³/Kg | Specific Volume ( v ) | 0.98228 | m³/Kg
| Enthalpy ( H ) | 54.0505 | Kj/Kg |  | Enthalpy ( H ) |  | 54.0505 | Kj/Kg | Enthalpy ( H ) | 54.0505 | Kj/Kg
| Sigma Heat ( S ) | 53.4966 | Kj/Kg |  | Sigma Heat ( S ) |  | 53.4966 | Kj/Kg | Sigma Heat ( S ) | 53.4966 | Kj/Kg
| Relative Humidity | 18.9614 | % |  | Relative Humidity |  | 18.9614 | % | Relative Humidity | 18.9614 | %
| Dewpoint Temp °C (tdp ) | 5.099 | °C |  | Dewpoint Temp °C (tdp ) |  | 5.099 | °C | Dewpoint Temp °C (tdp ) | 5.099 | °C
| Condenser Tower Discharge Air Out |  |  |  | Pre Cooling Tower Discharge Air Out |  |  |  | BAC Tower Discharge Air Out
| Wet Bulb Temp °C | 25.8 | °C |  | Wet Bulb Temp °C |  | 21.5 | °C | Wet Bulb Temp °C | 7.5 | °C
| Dry Bulb Temp °C | 29.8 | °C |  | Dry Bulb Temp °C |  | 24 | °C | Dry Bulb Temp °C | 7.5 | °C
| BP | 91.1 | Kpa |  | BP |  | 91.1 | Kpa | BP | 91.1 | Kpa
| Density ( w ) | 1.0344 | Kg/m³ |  | Density ( w ) |  | 1.0575 | Kg/m³ | Density ( w ) | 1.1262 | Kg/m³
| Vapour Press (Pw) | 3.0856 | Kpa |  | Vapour Press (Pw) |  | 2.4165 | Kpa | Vapour Press (Pw) | 1.0363 | Kpa
| Moisture Content ( r ) | 0.021806 | g/Kg |  | Moisture Content ( r ) |  | 0.016949 | g/Kg | Moisture Content ( r ) | 0.0071567 | g/Kg
| Moisture Content ( g/Kg ) | 21.806 | g/Kg |  | Moisture Content ( g/Kg ) |  | 16.9485 | g/Kg | Moisture Content ( g/Kg ) | 7.1567 | g/Kg
| Specific Volume ( v ) | 0.98787 | m³/Kg |  | Specific Volume ( v ) |  | 0.96164 | m³/Kg | Specific Volume ( v ) | 0.89433 | m³/Kg
| Enthalpy ( H ) | 85.6555 | Kj/Kg |  | Enthalpy ( H ) |  | 67.2405 | Kj/Kg | Enthalpy ( H ) | 25.5331 | Kj/Kg
| Sigma Heat ( S ) | 83.3038 | Kj/Kg |  | Sigma Heat ( S ) |  | 65.7173 | Kj/Kg | Sigma Heat ( S ) | 25.3087 | Kj/Kg
| Relative Humidity | 73.5968 | % |  | Relative Humidity |  | 81.0236 | % | Relative Humidity | 100 | %
| Dewpoint Temp °C (tdp ) | 15.4657 | °C |  | Dewpoint Temp °C (tdp ) |  | 13.0046 | °C | Dewpoint Temp °C (tdp ) | 4.8382 | °C
| Duty Calculation |  |  |  | Duty Calculation |  |  |  | Duty Calculation
| Sigma Heat OUT | 83.3038 | Kj/Kg |  | Sigma Heat OUT |  | 65.7173 | Kj/Kg | BAC Air IN | 53.4966 | Kj/Kg
| Sigma Heat IN | 53.4966 | Kj/Kg |  | Sigma Heat IN |  | 53.4966 | Kj/Kg | BAC Air OUT | 25.3087 | Kj/Kg
| Density Air In | 1.0255 | Kg/m³ |  | Density Air In |  | 1.0255 | Kg/m³ | Density Air In | 1.0255 | Kg/m³
| Quantity of Air (If it cannot be measured, use design) | 200 | m³/s |  | Quantity of Air |  | 150 | m³/s | Quantity of Air | 220 | m³/s
| DUTY (KW) | 6113.6514 | Kj/s |  | DUTY (KW) |  | 1879.9067 | Kj/s | DUTY (KW) | 6359.6894 | Kj/s
| Massflow (kg/s) | 205.1067 | Kg/s |  | Massflow (kg/s) |  | 153.83 | Kg/s | Massflow (kg/s) | 225.6173 | Kg/s

## Comp Air
Back to INDEX
Note: Data Books can be purchased from MVS Contact Number 011 482 7957
Pressure Loss through Piping for Air |  |  |  |  | Pressure Loss through Piping for Air
Equation(s) |  |  |  |  | Equation(s) : Corrected Pressure loss per m = Rate of PL (from Graph) x Pressure Correction x Temperature Correction
L = (in meters) | 3000 | m | Enter |  | Rate of PL - Massflow rate (from Graph) | 0.2 | kPa/m | Enter
v = Velocity (m/s) | 20 | m/s | Enter |  | Pressure Correction | 1 | kPa | Enter
ρ = Density of air (kg/m³) | 1.29 | Kg/m³ | Enter |  | Temperature Correction | 1 | °C | Enter
μ = Coefficient of friction | 0.0032 | ns²/m⁸ | Enter |  | L = (in meters) | 25 | m | Enter
d = Pipe Inner Diameter (m) | 150 | mm | Enter |  | d = Pipe Inner Diameter (m) | 0.05 | m | Enter
d = Pipe Inner Diameter (m) | 0.15 | m | Enter |  | Corrected Pressure loss per m | 0.2 | kPa/m
 Pressure Loss (Pa) | 16512Pa |  |  | 16512 | Total Pressure Loss | 5 | kPa
 Pressure Loss (KPa) | 16.512 | KPa
 Pressure Loss (MPa) | 0.016512 | MPa
Air Flow Rate through Piping
Equation(s)
d = Pipe Inner Diameter (m)
v = Air Velocity (m/s)
Qa = Air Flow Rate (Actual) (m³/min)
d = Pipe Inner Diameter (mm) | 50 | mm
d = Pipe Inner Diameter (m) | 0.05 | m
v = Air Velocity (m/s) | 20 | m/s
Air Flow Rate (Actual) (m³/min) | 2.3562 | m³/min
| 0.03927 | m³/s
Steel Pipes | Nominal pipe diameter (mm) | Resistance Factor
| 25 | 3000000
| 50 | 66000
| 100 | 1700
| 150 | 200
| 200 | 45
| 250 | 14
| 300 | 5.3
| 350 | 2.3
| 400 | 1.2
| 450 | 0.63
| 500 | 0.36
| 550 | 0.22
| 600 | 0.14
| 650 | 0.093
| 700 | 0.063
Rubber Hoses | 25 | 2000000
| 30 | 500000
Effect of auto compression
Equation(s)
Ps = absolute pressure at Start of column [kPa] |  | 600 | kPa | Enter
H = vertical depth metres [m] |  | 1600 | m | Enter
R = gas constant J/kgK [287 J/kgK] |  | 287 | J/kgK | Enter
G = gravitational acceleration m/s2 [9.79 m/s2] |  | 9.79 | m/s² | Enter
T = absolute temperature [K] |  | 273 | K | Enter
Pe = absolute pressure at End of column [kPa] |  | 732.7837 | Pa

## Water
Back to INDEX
Temperature Increase In Pipes
· Vertical pipes (Stroh’s Equation)
Dt | = | per 1000 m = |  |  | 2.3382 | °C per 1000 m
Start Water Temp |  |  | 1 | °C
Start depth |  |  | 0 | m
End depth |  |  | 3052 | m
Δd |  |  | 3052 | m
°C Water Temp gain |  |  | 7.1362 | °C
End Water Temp |  |  | 8.1362 | °C
Pump Power Requirements
Power =
| H - Total head [m] |  |  | 450 | m | Enter
| Q - Volume flow rate |  |  | 60 | ℓ/s | Enter
| SG - Specific gravity |  |  | 1 | [kg/m³
| g - Gravitational acceleration |  |  | 9.79 | m/sec²
| Pump efficiency expressed as a fraction of 1 [i.e. %] |  |  | 800 |  | NOTE : Pump Efficiency 100% = 1000 - 80% = 800 etc.
|  | Power |  | 330.4125 |  | kW
Pump Efficiency
|  | Efficiency | =
Power output is determined by the following equation:-
| Q - Volume flow rate |  |  | 60 | ℓ/s | Enter
| HT - Total head [m] |  |  | 450 | m | Enter
| g - Gravitational acceleration |  |  | 9.79 | m/sec²
| SG - Specific gravity |  |  | 1 | [kg/m³
|  | Power output |  | 264.33 |  | kW
| THUS | Efficiency | = | Power Input |  | 300 | kW
|  |  |  | Power Output |  | 264.33 | kW
|  |  | Pump Efficiency |  |  | 88.11 | %
Fissure Water Calculation
|  | Planning Parameter |  | 0.4 | t/t
|  | Design tons |  | 110 | kt/m
| Tons per month = |  |  | 110000 | t/m
| Tons water per month = |  |  | 44000 | t/m
| Tons water per day = |  |  | 1692.3077 | t/day
| Tons water per hour = |  |  | 70.5128 | t/hour
| Tons water per min = |  |  | 1.1752 | t/min
| Tons water per second = |  |  | 0.019587 | t/sec
1 ton water = 1000 liter
| Liters per second = |  |  | 19.5869 | l/s

## Fans
Back to INDEX
| w = |  | w = |  | w = |  | w = |  | w = |  | w = |  | w = | Resistance ('R) | 405.6247 | Ns4/m8 | Enter Value!!
1.1kW fan | 1.2 | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.3
Volume (m³/s) | Pressure (pa) | Pressure 10° (pa) | Pressure 10° (pa) | Pressure 15° (pa) | Pressure 15° (pa) | Pressure 20° (pa) | Pressure 20° (pa) | Pressure 25° (pa) | Pressure 25° (pa) | Pressure 30° (pa) | Pressure 30° (pa) | Pressure 35° (pa) | Pressure 35° (pa) | 1.1Kw fan | w = 1.2
0.01 | 640 | 620 | 671.6667 | 700 | 758.3333 | [8 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
0.5 | 480 | 500 | 541.6667 | 580 | 628.3333 | 620 | 671.6667 | [6 empty] | 0 |  | 0
1 | 300 | 330 | 357.5 | 440 | 476.6667 | 520 | 563.3333 | [6 empty] | 0.5 |  | 101.4062
1.3 | 0 | 130 | 140.8333 | 280 | 303.3333 | 420 | 455 | 490 | 530.8333 | 500 | 541.6667 |  |  | 1 |  | 405.6247
1.5 |  |  |  | 0 |  | 300 | 325 | 420 | 455 | 455 | 492.9167 | 490 | 530.8333 | 1.3 |  | 685.5057
1.8 | [5 empty] | 0 | 0 | 300 | 325 | 380 | 411.6667 | 420 | 455 | 1.5 |  | 912.6555
2 | [7 empty] | 130 | 140.8333 | 280 | 303.3333 | 350 | 379.1667 | 1.8 |  | 1314.2239
2.3 | [7 empty] | 0 | 0 | 130 | 140.8333 | 230 | 249.1667 | 2 |  | 1622.4986
2.5 | [9 empty] | 0 | 0 | 100 | 108.3333 | 2.3 |  | 2145.7545
3 | [11 empty] | 0 | 0 | 2.5
[8 empty] | Resistance ('R) | 55 | Ns4/m8 | Enter Value!!
4kW fan | w = 1.2
Volume (m³/s) | Pressure (pa) | [6 empty] | 4Kw fan | w = 1.2
1 | [7 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
2 | [7 empty] | 1 | 2400 | 55
3 | 1200 | [6 empty] | 2 | 2200 | 220
4 | 900 | [6 empty] | 3 | 2050 | 495
5 | 0 | [6 empty] | 4 | 1800 | 880
[8 empty] | 5 | 1650 | 1375
[8 empty] | Resistance ('R) | 55 | Ns4/m8 | Enter Value!!
8kW fan | w = 1.2
Volume (m³/s) | Pressure (pa) | [6 empty] | 8Kw fan | w = 1.2
1 | [7 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
2 | [7 empty] | 1 | 2400 | 55
3 | 1200 | [6 empty] | 2 | 2200 | 220
4 | 900 | [6 empty] | 3 | 2050 | 495
5 | 0 | [6 empty] | 4 | 1800 | 880
[8 empty] | 5 | 1650 | 1375
[8 empty] | Resistance ('R) | 60 | Ns4/m8 | Enter Value!!
11kW fan | w = 1.2
Volume (m³/s) | Pressure (pa) | [6 empty] | 11Kw fan | w = 1.2
1 | [7 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
2 | [7 empty] | 1 | 2400 | 60
3 | [7 empty] | 2 | 2200 | 240
4 | 1500 | [6 empty] | 3 | 2050 | 540
5 | 1150 | [6 empty] | 4 | 1800 | 960
6 | 400 | [6 empty] | 5 | 1650 | 1500
[8 empty] | 6 | 1700 | 2160
[8 empty] | Resistance ('R) | 55 | Ns4/m8 | Enter Value!!
15kW fan | w = 1.2
Volume (m³/s) | Pressure (pa) | [6 empty] | 15Kw fan | w = 1.2
[8 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
4.5 | 1540 | [6 empty] | 1 | 2400 | 55
5 | 1450 | [6 empty] | 2 | 2200 | 220
5.5 | 1200 | [6 empty] | 3 | 2050 | 495
6 | 900 | [6 empty] | 4 | 1800 | 880
6.5 | 550 | [6 empty] | 5 | 1650 | 1375
7 | 220 | [6 empty] | 6 | 1700 | 1980
7.2 | 0 | [6 empty] | 7 | 1800 | 2695
[8 empty] | Resistance ('R) | 55 | Ns4/m8 | Enter Value!!
[8 empty] | 18Kw fan | w = 1.2
18kW fan | w = 1.2 | [6 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
Volume (m³/s) | Pressure (pa) | [6 empty] | 1 | 2400 | 55
1 | [7 empty] | 2 | 2200 | 220
2 | [7 empty] | 3 | 2050 | 495
3 | [7 empty] | 4 | 1800 | 880
4 | 2000 | [6 empty] | 5 | 1650 | 1375
5 | 1950 | [6 empty] | 6 | 1700 | 1980
6 | 1750 | [6 empty] | 7 | 1800 | 2695
7 | 1350 | [6 empty] | 8 | 1700 | 3520
8 | 650
8.5 | 0
[8 empty] | Resistance ('R) | 55 | Ns4/m8 | Enter Value!!
[8 empty] | 22Kw fan | w = 1.2
22kW fan | w = 1.2 | [6 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
Volume (m³/s) | Pressure (pa) | [6 empty] | 1 | 2400 | 55
7 | 1800 | [6 empty] | 2 | 2200 | 220
8 | 1680 | [6 empty] | 3 | 2050 | 495
9 | 1360 | [6 empty] | 4 | 1800 | 880
10 | 900 | [6 empty] | 5 | 1650 | 1375
11 | 450 | [6 empty] | 6 | 1700 | 1980
12 | 0 | [6 empty] | 7 | 1800 | 2695
[8 empty] | 8 | 1700 | 3520
[8 empty] | 9 | 1300 | 4455
[8 empty] | 10 | 800
[8 empty] | 11 | 0
Resistance ('R) | 41 | Ns4/m8 | Enter Value!!
Fan Dia | 0.76 | m | [6 empty] | Resistance ('R) | 45 | Ns4/m8 | Enter Value!!
C= | 2.3876 | m
45kW fan | w = 1.2
Volume (m³/s) | Pressure (pa) | Resistance (pa) | [6 empty] | 2 x 45Kw fan | w = 1.2
|  | 0 | [6 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
9 |  | 3321
10 | 2400 | 4100
11 | 2350 | 4961
12 | 2000 | 5904 | [6 empty] | 10 | 7200 | 4500
13 | 1400 | 6929 | [6 empty] | 11 | 7050 | 5445
14 | 850 | 8036 | [6 empty] | 12 | 6000 | 6480
15 | 300 | 9225 | [6 empty] | 13 | 4200 | 7605
16 | 0 | 10496 | [6 empty] | 14 | 2550 | 8820
[9 empty] | 15 | 900 | 10125 | [6 empty] | 1 | 2 | 3 | 4 | 5 | Fans in Series
[9 empty] | 16 | 0 | [7 empty] | 2400 | 4800 | 7200 | 9600 | 12000
[18 empty] | 2350 | 4700 | 7050 | 9400 | 11750
[18 empty] | 2000 | 4000 | 6000 | 8000 | 10000
[18 empty] | 1400 | 2800 | 4200 | 5600 | 7000
[18 empty] | 850 | 1700 | 2550 | 3400 | 4250
[18 empty] | 300 | 600 | 900 | 1200 | 1500
[18 empty] | 0 | 0 | 0 | 0 | 0
[8 empty] | Resistance ('R) | 21 | Ns4/m8 | Enter Value!!
55kW fan | w = 1.2
Volume (m³/s) | Pressure (pa) | [6 empty] | 45Kw fan | w = 1.2
[8 empty] | Volume (m³/s) | Pressure (pa) | Resistance (pa)
[8 empty] | 4 |  | 336
[8 empty] | 5 |  | 525
[8 empty] | 6 |  | 756
[8 empty] | 7 |  | 1029
[8 empty] | 8 |  | 1344
[8 empty] | 9 |  | 1701
[8 empty] | 10 |  | 2100
11 | 2950 | [6 empty] | 11 | 2950 | 2541
12 | 2800 | [6 empty] | 12 | 2800 | 3024
13 | 2500 | [6 empty] | 13 | 2500 | 3549
14 | 2080 | [6 empty] | 14 | 2080 | 4116
15 | 1450 | [6 empty] | 15 | 1450 | 4725
16 | 960 | [6 empty] | 16 | 960 | 5376
17 | 330 | [6 empty] | 17 | 330 | 6069
17.5 | 0 | [6 empty] | 17.5 | 0 | 6431.25
[8 empty] | Resistance ('R) | 9.1 | Ns4/m8 | Enter Value!!
75kW fan | w = 1.4
Volume (m³/s) | Pressure (pa) | [6 empty] | 75Kw fan | w = 1.2
1 | [7 empty] | Volume (m³/s) | Pressure (pa) | Series Fan (pa) | Resistance (pa)
2 | [7 empty] | 1 |  |  | 9.1
3 | [7 empty] | 2 |  |  | 36.4
4 | [7 empty] | 3 |  |  | 81.9
5 | [7 empty] | 4 |  |  | 145.6
6 | [7 empty] | 5 |  |  | 227.5
7 | [7 empty] | 6 |  |  | 327.6
8 | [7 empty] | 7 |  |  | 445.9
9 | [7 empty] | 8 |  |  | 582.4
10 | [7 empty] | 9 |  |  | 737.1
11 | [7 empty] | 10 |  |  | 910
12 | [7 empty] | 11 |  |  | 1101.1
13 | [7 empty] | 12 |  |  | 1310.4
14 | [7 empty] | 13 |  |  | 1537.9
15 | [7 empty] | 14 |  |  | 1783.6
16 | [7 empty] | 15 |  |  | 2047.5
17 | 2360 | [6 empty] | 16 |  |  | 2329.6
18 | 2310 | [6 empty] | 17 | 2360 | 4720 | 2629.9
19 | 2220 | [6 empty] | 18 | 2310 | 4620 | 2948.4
20 | 2040 | [6 empty] | 19 | 2220 | 4440 | 3285.1
21 | 1815 | [6 empty] | 20 | 2040 | 4080 | 3640
22 | 1580 | [6 empty] | 21 | 1815 | 3630 | 4013.1
23 | 1300 | [6 empty] | 22 | 1580 | 3160
24 | 1000 | [6 empty] | 23 | 1300 | 2600
25 | 680 | [6 empty] | 24 | 1000 | 2000
26 | 350 | [6 empty] | 25 | 680 | 1360
27 | 0 | [6 empty] | 26 | 350 | 700
[8 empty] | 27 | 0 | 0
CREATE YOUR OWN!!
Resistance ('R) |  | 0.3 |  | Ns4/m8 | Enter Value!!
ENTER FAN DATA
FAN | w = 1.2
Volume (m³/s) | Pressure (pa) | Resistance (pa)
60 | 4900 | 1080
70 | 5000 | 1470
80 | 4930 | 1920
90 | 4500 | 2430
100 | 3890 | 3000
110 | 3180 | 3630
120 | 2400 | 4320
130 | 1630 | 5070
140 | 810
150 | 0
Resistance ('R) |  | 1.15 |  | Ns4/m8 | Enter Value!!
ENTER FAN DATA
FAN | w = 1.2
Volume (m³/s) | Pressure (pa) | Resistance (pa)
22 | 1660 | 556.6
24 | 1680 | 662.4
26 | 1650 | 777.4
28 | 1480 | 901.6
30 | 1300 | 1035
32 | 1150 | 1177.6
34 | 1050 | 1329.4
36 | 950 | 1490.4
55kW fan
Resistance ('R) |  | 6.162 |  | Ns4/m8 | Enter Value!!
ENTER FAN DATA
FAN | w = 1.2
Volume (m³/s) | Pressure (pa) | Resistance (pa)
20 | 3850 | 2464.8
22 | 3900 | 2982.408
24 | 3750 | 3549.312
26 | 3350 | 4165.512
28 | 2650 | 4831.008
30 | 1850
32 | 1150
34 | 500
36 | 0
110kW Fan @ 35°
| w = | 1.1 | Kg/m³
| Duct Length | 500 | m
| K- Factor | 0.0037 | ns²/m⁴ | C = | 3.7699 | m
Duct Diameter (m) |  | 1.2 |  | A = | 1.131 | m²
Resistance ('R) |  | 4.4193 |  | Ns4/m8
ENTER FAN DATA
FAN | w = 1.2
Volume (m³/s) | Pressure (pa) | Resistance (pa)
0 |  | 0
2 |  | 17.6773
4 |  | 70.7094
6 |  | 159.0961
8 |  | 282.8376
10 |  | 441.9337
12 |  | 636.3846
14 |  | 866.1901
16 |  | 1131.3504
18 | 2825 | 1431.8653
20 | 2650 | 1767.735
22 | 2400 | 2138.9593
24 | 2000 | 2545.5384
26 | 1550 | 2987.4721
28 | 1100 | 3464.7606
30 | 600 | 3977.4037
31.5 | 0 | 4385.0876
Note on D239: Jvansittert: Copy/paste & Delete formulaes as required
Note on D240: Jvansittert: Copy/paste & Delete formulaes as required
Note on D241: Jvansittert: Copy/paste & Delete formulaes as required
Note on D242: Jvansittert: Copy/paste & Delete formulaes as required
Note on D243: Jvansittert: Copy/paste & Delete formulaes as required
Note on D244: Jvansittert: Copy/paste & Delete formulaes as required
Note on D245: Jvansittert: Copy/paste & Delete formulaes as required
Note on D246: Jvansittert: Copy/paste & Delete formulaes as required
Note on D247: Jvansittert: Copy/paste & Delete formulaes as required
Note on D248: Jvansittert: Copy/paste & Delete formulaes as required
Note on D249: Jvansittert: Copy/paste & Delete formulaes as required
Note on D250: Jvansittert: Copy/paste & Delete formulaes as required
Note on D251: Jvansittert: Copy/paste & Delete formulaes as required
Note on D252: Jvansittert: Copy/paste & Delete formulaes as required
Note on D253: Jvansittert: Copy/paste & Delete formulaes as required
Note on D254: Jvansittert: Copy/paste & Delete formulaes as required
Note on D255: Jvansittert: Copy/paste & Delete formulaes as required
Note on D275: Jvansittert: Copy/paste & Delete formulaes as required
Note on D276: Jvansittert: Copy/paste & Delete formulaes as required
Note on D277: Jvansittert: Copy/paste & Delete formulaes as required
Note on D278: Jvansittert: Copy/paste & Delete formulaes as required
Note on D279: Jvansittert: Copy/paste & Delete formulaes as required
Note on D280: Jvansittert: Copy/paste & Delete formulaes as required
Note on D281: Jvansittert: Copy/paste & Delete formulaes as required
Note on D282: Jvansittert: Copy/paste & Delete formulaes as required
Note on D283: Jvansittert: Copy/paste & Delete formulaes as required
Note on D284: Jvansittert: Copy/paste & Delete formulaes as required
Note on D285: Jvansittert: Copy/paste & Delete formulaes as required
Note on D286: Jvansittert: Copy/paste & Delete formulaes as required
Note on D287: Jvansittert: Copy/paste & Delete formulaes as required
Note on D288: Jvansittert: Copy/paste & Delete formulaes as required
Note on D289: Jvansittert: Copy/paste & Delete formulaes as required
Note on D290: Jvansittert: Copy/paste & Delete formulaes as required
Note on D291: Jvansittert: Copy/paste & Delete formulaes as required
Note on D310: Jvansittert: Copy/paste & Delete formulaes as required
Note on D311: Jvansittert: Copy/paste & Delete formulaes as required
Note on D312: Jvansittert: Copy/paste & Delete formulaes as required
Note on D313: Jvansittert: Copy/paste & Delete formulaes as required
Note on D314: Jvansittert: Copy/paste & Delete formulaes as required
Note on D315: Jvansittert: Copy/paste & Delete formulaes as required
Note on D316: Jvansittert: Copy/paste & Delete formulaes as required
Note on D317: Jvansittert: Copy/paste & Delete formulaes as required
Note on D318: Jvansittert: Copy/paste & Delete formulaes as required
Note on D319: Jvansittert: Copy/paste & Delete formulaes as required
Note on D320: Jvansittert: Copy/paste & Delete formulaes as required
Note on D321: Jvansittert: Copy/paste & Delete formulaes as required
Note on D322: Jvansittert: Copy/paste & Delete formulaes as required
Note on D323: Jvansittert: Copy/paste & Delete formulaes as required
Note on D324: Jvansittert: Copy/paste & Delete formulaes as required
Note on D325: Jvansittert: Copy/paste & Delete formulaes as required
Note on D326: Jvansittert: Copy/paste & Delete formulaes as required
Note on D349: Jvansittert: Copy/paste & Delete formulaes as required
Note on D350: Jvansittert: Copy/paste & Delete formulaes as required
Note on D351: Jvansittert: Copy/paste & Delete formulaes as required
Note on D352: Jvansittert: Copy/paste & Delete formulaes as required
Note on D353: Jvansittert: Copy/paste & Delete formulaes as required
Note on D354: Jvansittert: Copy/paste & Delete formulaes as required
Note on D355: Jvansittert: Copy/paste & Delete formulaes as required
Note on D356: Jvansittert: Copy/paste & Delete formulaes as required
Note on D357: Jvansittert: Copy/paste & Delete formulaes as required
Note on D358: Jvansittert: Copy/paste & Delete formulaes as required
Note on D359: Jvansittert: Copy/paste & Delete formulaes as required
Note on D360: Jvansittert: Copy/paste & Delete formulaes as required
Note on D361: Jvansittert: Copy/paste & Delete formulaes as required
Note on D362: Jvansittert: Copy/paste & Delete formulaes as required
Note on D363: Jvansittert: Copy/paste & Delete formulaes as required
Note on D364: Jvansittert: Copy/paste & Delete formulaes as required
Note on D365: Jvansittert: Copy/paste & Delete formulaes as required

## FAN LAWS
FAN LAWS |  |  |  |  | Back to INDEX
NOTE:
Fan Speed Change - Qty Change
Fan Speed 1 |  |  | 1470 | rpm | Enter
Fan Speed 2 |  |  | 1029 | rpm | Enter
Quantity 1 |  |  | 25 | m³/s | Enter
Quantity 2 |  |  | 17.5 | m³/s |  |  | Fan Speed | Fan rpm | Fan Speed | Fan rpm | Fan Speed | Fan rpm | Fan Speed | Fan rpm
[7 empty] | 100% | 1470 | 40% | 588 | 50% | 735 | 70% | 1029
[7 empty] | Volume (m³/s) | SP (Pa) @ Design kg/m³ | Volume (m³/s) | SP (Pa) @ Design kg/m³ | Volume (m³/s) | SP (Pa) @ Design kg/m³ | Volume (m³/s) | SP (Pa) @ Design kg/m³
Fan Speed Change - Pressure Change | [6 empty] | 25 | 1480 | 10 | 236.8 | 12.5 | 370 | 17.5 | 725.2
[7 empty] | 27.5 | 1320 | 11 | 211.2 | 13.75 | 330 | 19.25 | 646.8
[7 empty] | 30 | 1140 | 12 | 182.4 | 15 | 285 | 21 | 558.6
[7 empty] | 32.5 | 950 | 13 | 152 | 16.25 | 237.5 | 22.75 | 465.5
[7 empty] | 35 | 550 | 14 | 88 | 17.5 | 137.5 | 24.5 | 269.5
[7 empty] | 38 | 0 | 15.2 | 0 | 19 | 0 | 26.6 | 0
[9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Fan Speed 1 |  |  | 1470 | rpm | Enter
Fan Speed 2 |  |  | 1029 | rpm | Enter
Fan Pressure 1 |  |  | 1250 | Pa | Enter
Fan Pressure 2 |  |  | 612.5 | Pa
Fan Speed Change - Power Change
Single Belt Transmission - one driving pulley and one driven pulley
For a system with two shafts and two pulleys - as indicated with pulley 1 and 2 in the figure above:
d1 n1= d2 n2 (1)
where
Fan Speed 1 |  |  | 1470 | rpm | Enter
Fan Speed 2 |  |  | 1029 | rpm | Enter |  |  | d1 = driving pulley diameter (inch, mm)
Fan Power 1 |  |  | 780 | kW | Enter
Fan Pressure 2 |  |  | 267.54 | kW |  |  |  | n1 = revolutions of driving pulley (rpm - rounds per minute)
d2 = driven pulley diameter (inch, mm)
FAN PULLEY SIZE CHANGES
n2 = revolutions of driven pulley (rpm - rounds per minute)
Equation (1) can be transformed to express the
Revolution of Driven Pulley
n2 = d1 n1 / d2 (2)
Fan Speed 1 (Old Speed) |  |  | 1470 | rpm | Enter
Fan Speed 2 (New Speed) |  |  | 1029 | rpm | Enter |  |  | Revolution of Driver Pulley
Old pulley size |  |  | 250 | mm | Enter |  |  | n1 = d2 n2 / d1 (3)
New pulley size |  |  | 357.1429 | mm
Diameter of Driven Pulley
d2 = d1 n1 / n2 (4)
MOTOR PULLEY SIZE CHANGES
Diameter of Driver Pulley
d1 = d2 n2 / n1 (5)
Multiple Belt Transmission Systems
For a system a with three shafts and four pulleys - as indicated in the figure above:
Motor Speed 1 (Old Speed) |  |  | 3700 | rpm | Enter |  |  | n2 = n3 (6)
Motor Speed 2 (New Speed) |  |  | 1000 | rpm | Enter
Old pulley size |  |  | 200 | mm | Enter |  |  | n4 = n1 (d1 d3) / (d2 d4) (7)
New pulley size |  |  | 54.0541 | mm
Example - Multiple Belt Transmission System
The revolutions of shaft 4 in a multiple belt transmission like indicated in the figure above where
n1 = 1000 rpm
Fan Efficiency Calc
d1 = 100 mm
| Enter Fan Pressure |  |  | 3700 | Pa
| Enter Fan Volume |  |  | 270 | m³/s |  |  | d2 = 50 mm
| Enter Fan Motor Input Power |  |  | 1511 | kW
| Fan Efficiency |  |  | 66.12% | Eff |  |  | d3 = 110 mm
d4 = 60 mm
can be calculated as
n4 =(1000 rpm) (100 mm) (110 mm) / ((50 mm) (60 mm))
Running Cost -(Known kW) Partial Hours or Shifts
= 3667 rpm
| Enter Fan Kw | 951 | kW
| c/kWh | 181
| Hours per day | 24
| Shifts per month | 30
| Cost / Month | 1239343.2 | Rand
Note on D86: Get this Cost from Eskom website / Costing Dept

## Trig & Volume
| Right Triangle Solver | [8 empty] | Back to INDEX
[23 empty] | H1 |  | H
| Enter ONLY TWO known pieces of information | [13 empty] | A=(πab)4 |  |  |  |  | A=(πab)4
[5 empty] | Length |  |  | Degrees | [6 empty] | Yc=4b/3π |  |  |  |  | Yc=4b/3π |  |  |  | W | Area Arched Tunnel (Bottom)
[5 empty] | a | b | c | Y | Z | Area and Volume |  |  |  |  | Area Semi-elipse |  |  |  |  | Area Arched Tunnel (Top) |  |  |  |  | Width (W) | 5.3 | m | Enter
| a= | 5.5 | m |  |  |  |  | 45 | 45 | Parameters |  |  |  |  | b = | 0.5 | mm / m | Enter |  | b = | 1.3 | mm / m | Enter |  | Height (H1) | 4.5 | m | Enter
| b= | 5.5 | m | [6 empty] | Pipe / Tube Length | 0.6 | m |  |  | a = | 1.5 | mm / m | Enter |  | a = | 2.65 | mm / m | Enter |  | Height (H) | 5.8 | m
| c= |  | m |  | 0 |  |  |  |  | Pipe / Tube Diameter | 4 | m |  |  | y = | 0.21221 | mm / m |  |  | y = | 0.55174 | mm / m |  |  | C = | 14.3 | m
[10 empty] | Area (circle) | 12.5664 | m² |  |  | A = | 0.96589 | mm² / m² | 9.6589e-07 |  | C = | 5.4114 | mm / m |  |  | A = | 23.85 | m²
| X= | 90 | º |  | 5.5 | 5.5 | 7.7782 | 45 |  | Total Area (cylinder) | 32.6726 | m² |  |  | C = | 1.1781 | mm / m | 0.0011781 |  | A = | 4.8597 | mm² / m² |  |  | TOTAL C = | 19.7114 | m
| Y= |  | º |  |  |  |  | 45 |  | Total Area (pipe) | 7.5398 | m² |  | http://www.1728.org/ellipse.htm |  |  |  |  | http://www.1728.org/ellipse.htm | [5 empty] | TOTAL A = | 28.7097 | m²
| Z= | 45 | º | [6 empty] | C = | 12.5664 | m
[5 empty] | Degree Converter |  |  |  |  | Volume | 7.5398 | m³/s |  |  | Pre Calculated Round Arch and Flat Arched tunnels
[5 empty] | Degrees entered as a decimal will be converted to Deg, Min, Sec |  |  |  |  | Volume | 7.5398 | Mega Litre
[5 empty] | 6 | Degrees (°) | 6 | 6 | Degrees | Volume | 7539.8224 | Litre
| Y |  |  |  | 0.41667 | Minutes (min) | 25 | 25 | Minutes
[5 empty] | 0.0027778 | Seconds (sec) | 10 | 10 | Seconds | Area and Volume
|  |  | c |  | 6.4194 |  |  | Angle as a decimal
| a |  |  |  |  | NOTE: | The Degree Converter above has |  |  | Parameters
[7 empty] | no influence on the Right Triangle |  |  | Tunnel Length | 0.55 | m
[5 empty] | Z |  | calculations. |  |  | Tunnel Width | 0.55 | m
| X |  | b | [6 empty] | Tunnel Height | 0.55 | m
[10 empty] | Area (Square) | 0.3025 | m²
[10 empty] | Total Area (cube) | 1.815 | m²
[10 empty] | Total Area (Tube) | 1.21 | m²
[10 empty] | Volume | 0.16638 | m³
[10 empty] | Volume | 0.16638 | Mega Litre
[10 empty] | Volume | 166.375 | Litre
Diameter from Circumference
[10 empty] | Distance between sections | 12.7 | mm / m
[10 empty] | Sections | 10 | Each
[10 empty] | C = | 127 | mm / m
[7 empty] | 455.6 | m |  | Pipe Radius= | 20.2127 | mm / m
[10 empty] | Pipe Diameter = | 40.4254 | mm / m
[8 empty] | 455.6 |  | Diameter from Area
2603.2
[10 empty] | Pipe Area | 0.255 | mm² / m²
[10 empty] | Pipe Diameter = | 0.5698 | mm / m
Adjacent (A) Angle (if distances are known)
Adjacent (A) Length | 2603.2 | m | 9.927 | º |  | 9.9271 | º
|  | AB (H) = | 2642.7862 | m
|  | Radians | 0.17239
Speed - Distance - Time
|  | Distance |  |  |  | 500 | km | Enter
|  | Average Speed |  |  |  | 100 | km/h | Enter
|  | Time |  |  |  | 300 | minutes
|  | Hours |  |  |  | 5 | Hours
|  | Distance |  |  |  | 600 | km | Enter
|  | Hours |  |  |  | 5 | Hours | Enter
|  | Time |  |  |  | 300 | minutes
|  | Average Speed |  |  |  | 120 | km/h
Simple vent Calcs
Vel | Diameter | Area m² | Qty m³/s
10 | 3.1 | 7.5477 | 75.4768
10.1 | 3.1 | 7.5477 | 76.2315
12.8 | 3.1 | 7.5477 | 96.6103 |  | 20.3787
| 3.1 | 7.5477 | 0
|  | 0 | 0
8.7 | 1.65 | 2.1382 | 18.6027 |  | 74.411 | [5 empty] | Flat Arch | [5 empty] | Normal square tunnel
|  | 0 | 0 | [7 empty] | Width | Height | Perimeter | Area | Factor Area | Factor Perimeter | Perimeter (Hx2+Wx2) | Area(HxW)
|  | 0 | 0 | [7 empty] | 5.6 | 5.8 | 15.483 | 30.763 | 0.94714 | 0.67908 | 22.8 | 32.48
|  | 0 | 0 | [7 empty] | 8 | 6 | 17.94 | 45.223 | 0.94215 | 0.64071 | 28 | 48
|  | 0 | 0 | [7 empty] | 6 | 5.5 | 15.259 | 31.107 | 0.94264 | 0.66343 | 23 | 33
|  | 0 | 0 | [7 empty] | 5.6 | 5.5 | 14.91 | 29.038 | 0.94279 | 0.67162 | 22.2 | 30.8
|  | 0 | 0 | [7 empty] | 7 | 5.5 | 16.144 | 36.277 | 0.94226 | 0.64576 | 25 | 38.5
|  | 0 | 0 | [7 empty] | 6 | 5.8 | 15.86 | 32.894 | 0.94523 | 0.67203 | 23.6 | 34.8
|  | 0 | 0 | [6 empty] | Enter tunnel size: | 5.5 | 6 | 15.2285 | 31.1421 | 0.9437 | 0.66211 | 23 | 33
[11 empty] | Round Arch | [5 empty] | Normal square tunnel
[11 empty] | Width | Height | Perimeter | Area | Factor Area | Factor Perimeter | Perimeter (Hx2+Wx2) | Area(HxW)
[11 empty] | 4.5 | 4.5 | 11.569 | 18.077 | 0.89269 | 0.64272 | 18 | 20.25
[11 empty] | 5 | 5 | 12.857 | 22.324 | 0.89296 | 0.64285 | 20 | 25
[11 empty] | 5.5 | 5.5 | 14.139 | 27.004 | 0.89269 | 0.64268 | 22 | 30.25
[11 empty] | 4.8 | 4.8 | 12.34 | 20.568 | 0.89271 | 0.64271 | 19.2 | 23.04
[11 empty] | 7 | 7 | 17.996 | 43.742 | 0.89269 | 0.64271 | 28 | 49
[11 empty] | 8 | 8.5 | 21.566 | 61.133 | 0.89901 | 0.65352 | 33 | 68
[10 empty] | Enter tunnel size: | 5.5 | 5.8 | 14.5664 | 28.512 | 0.89379 | 0.64453 | 22.6 | 31.9
Calculating Pipe Fill Area
[10 empty] | Diameter (D) | 4.5 | m | Enter
[10 empty] | Radius | 2.25 | m
[10 empty] | Open Height (H) | 3.5 | m | Enter
[10 empty] | Filled Height (H) | 1 | m
[10 empty] | A = | 15.9043 | m²
[10 empty] | The Angle portion | 0.98177 | radians
[10 empty] | The Triangle portion | 2.3385 | m²
[10 empty] | Filled Space Area | 2.6317 | m²
[10 empty] | Open Area (at XXm height) | 13.2727 | m²
[10 empty] | Perimeter (P) | 9.7192 | m | Circumference
[10 empty] | #VALUE! | 15.9104 | m²
Adjacent (A)
Hypotenuse (H)
Opposite (O)

## Cost
Cost - | Water | [8 empty] | Back to INDEX
Power =
[7 empty] | 2024 |  | 28.5 | 21.3 | 5.7
| H - Total head [m] | 90 | m | Enter |  | Summer | 1.32 |  | 27.9 | 21.3 | 5.58
| Q - Volume flow rate | 20 | ℓ/s | Enter |  | Winter | 2.3 |  | 28.2 | 21.6 | 5.64 | 21.5
| SG - Specific gravity | 1 | [kg/m³ |  |  | Average | 1.81 |  | 26.8 | 20.2 | 5.36 | 129.5 | 144256
| g - Gravitational acceleration | 9.79 | m/sec² | [5 empty] | 27.6 | 21.4 | 5.52 | 11 |  |  |  |  | 21.5
| Pump efficiency expressed as a fraction of 1 [i.e. %] | 1000 | NOTE : Pump Efficiency 100% = 1000 - 80% = 800 etc. | [5 empty] | 28.4 | 20.6 | 5.68 | 48 | 388532.5077 |  | 8353448.9164 | 224100 | 129.4
| Power | 17.622 | kW | [5 empty] | 27.9 | 21.0667 |  | 16.7 | 868222 |  | 7964916.4087 | 144256 | 11
| Cost to Pump head above | [8 empty] | 6.8333 |  | 14 | 73806 |  | 388532.5077 | 368356 | 53.9
| c/kWh | 230 | c | Enter |  |  |  |  | 167.4 | 126.4 | 33.48 | 240.7 | 322061
| Cost / Month | 29182.032 | Rand | [6 empty] | 41 |  |  | 112051 |  |  | 1615001
| Cost / Annum | 350184.384 | Rand | [6 empty] | 33.48 |  |  | 93935 |  |  | 388532
[10 empty] | 7.52 |  |  | 2002863.5077 |  |  | 2003533
Cost - | Air
AIR POWER
|  | Wa = |  |  |  | OR |  | Wa =
"Jan 2020
84.54
| Pressure (P) | 3103 | Pa | Enter | 4000 |  |  | Resistance ('R) | 24 | ns²/m8 | Enter | [5 empty] | 84.54
| Qty (m³/s) | 454.4 | m³/s | Enter | 58 | 18 |  | Qty (m³/s) | 19.5 | m³/s | Enter | [5 empty] | 83.91
| Wa = | 1410.0032 | kW |  |  | 25 |  | Wa = | 177.957 | kW | [6 empty] | 78.56
| Fan Efficiency | 88 | % | Enter | 2246561 |  |  | Cost to Move Air above | [8 empty] | 82.8875
| Fan Ineff kW = | 192.2732 | kW |  |  |  |  | c/kWh | 185 | c | Enter
| Fan Input Power | 1602.2764 | kW |  | 8100 |  |  | Cost / Month | 237038.724 |  | Rand
| Cost to Move Air above |  |  |  | 7950
| c/kWh | 185 | c | Enter | 150 | [10 empty] | 3873417.7215
| Cost / Month | 2134232.1164 | Rand | [11 empty] | 343593 | 46481012.6582
| Fan Motor Efficiency | 95% |  |  | http://www.eskom.co.za/CustomerCare/TariffsAndCharges/Pages/Tariffs_And_Charges.aspx | [11 empty] | "Jan 2020
| Actual TOTAL Cost / Month | 2246561 | Rand | [13 empty] | 85.15
| TOTAL Cost / Annum | 26958732 | Rand | [13 empty] | 81.21
| Years | 10 | Yr |  | Power Saving |  |  |  | Value 1 | Value 2 | [6 empty] | 80.65
| Cost LOM (Years) | 269587320 | Rand |  |  |  |  | Pressure (P) | 1700 | 3480 | Pa | Enter |  |  |  |  | 75.47
[8 empty] | Qty (m³/s) | 90 | 90 | m³/s | Enter |  |  |  |  | 80.62
Running Cost -Fan (Known kW) | [7 empty] | Wa = | 153 | 313.2
[8 empty] | c/kWh | 185 | c | Enter
| Enter Fan Kw | 951 | kW |  |  |  |  | Fan Efficiency | 0.87 | % | Enter
| c/kWh | 181 | [5 empty] | Cost / Month | 234248.2759 | 479520
| Cost / Month | 1239343.2 | Rand |  |  |  |  | Saving | -104.7%
| Cost / Annum | 14872118.4 | Rand
Running Cost -(Known kW) Partial Hours or Shifts | [8 empty] | UG Fan 1 | UG Fan 2
[8 empty] | Pressure (P) | 784 | 1730 | Pa
| Enter Fan Kw | 951 | kW |  |  |  |  | Qty (m³/s) | 510 | 510 | m³/s
| c/kWh | 185 | [5 empty] | Wa = | 399.84 | 882.3
| Hours per day | 24 | [5 empty] | c/kWh | 185 | c | Enter
| Shifts per month | 30 | [5 empty] | Fan Efficiency | 0.87 | % | Enter
| Cost / Month | 1266732 | Rand |  |  |  |  | Cost / Month | 612168.8276 | 1350831.7241
-738662.8966
[8 empty] | Saving | -120.7%
Fan Efficiency Calc | [8 empty] | UG Fan 1 | UG Fan 2
[8 empty] | Pressure (P) | 784 | 1730 | Pa
| Enter Fan Pressure | 2300 | Pa |  |  |  |  | Qty (m³/s) | 510 | 510 | m³/s
| Enter Fan Volume | 310 | m³/s |  |  |  |  | Wa = | 399.84 | 882.3
| Enter Fan Motor Input Power | 907 | kW |  |  |  |  | c/kWh | 185 | c | Enter
| Fan Efficiency | 78.61% | Eff |  |  |  |  | Fan Efficiency | 0.87 | % | Enter
[8 empty] | Cost / Month | 612168.8276 | 1350831.7241
| or | [8 empty] | -738662.8966
[8 empty] | Increase in Running cost | 120.7%
| Enter Air Power | 500 | kW
| Enter Fan Motor Input Power | 907 | kW |  |  |  |  | -8863954.7586
| Fan Efficiency | 55.13% | Eff
Vent Pipe and Accessories Cost Estimator
| Hlge Advance |  |  |  |  | 45 | m
| RAW Advance |  |  |  |  | 45 | m
| Conn X/C x 1 Length |  |  |  |  | 30 | m
| Conn X/C 2 Due? Y=1 N=0 |  |  |  |  | 1
| Ventilation Collumn Lengths used |  |  |  |  | 2.21 | m | (Options - 2.24m 4.5m)
| 1015mm / 760mm Column Used |  |  |  |  | 760 | mm | Bolts per Pipe | 12
| Fans used Primary (kW) |  |  |  |  | 75 | kW
| Fans used Secondary (kW) |  |  |  |  | 45 | kW
| Equipment Replacement % |  |  |  |  | 0.1
[13 empty] | 45 | m
| Conn X/C 1 |  |  | 30 | m |  |  |  |  | Conn X/C 2 |  | 30 | m
[13 empty] | 45 | m
| Equipment |  |  |  |  | Quantity | Unit | Stock Codes | Cost per Unit | Total Cost
| 760 | mm Dia. Vent Pipes |  | 2.21 | m Lengths | 82.8733 | Each |  | 890.07 | 73763.041
| Bends 90° |  |  |  |  | 5 | Each |  |  | 0
| Bolts M12 x 50mm |  |  |  |  | 1094 | Each |  | 17.2 | 18816.8
| Bro Spray Waterblast |  |  |  |  | 3 | Each |  |  | 0
| Fans used Primary (kW) |  |  |  |  | 2 | Each |  |  | 0
| Fans used Secondary (kW) |  |  |  |  | 1 | Each |  |  | 0
| Suspension Chains 16mm for fans |  |  |  |  | 15 | m |  |  | 0
| Suspension Chains 10mm for Pipes |  |  |  |  | 829 | m |  |  | 0
| Pigtail Eyebolts (5 per fan) |  |  |  |  | 15 | Each |  | 48.48 | 727.2
| Pigtail Eyebolts (2 for every 4.5m) |  |  |  |  | 34 | Each |  | 48.48 | 1648.32
| "Y" Piece/Lateral (If Used) |  |  |  |  | 0 | Each |  | 1570 | 0
[6 empty] | 3 | Each |  |  | 0
| Total | [8 empty] | 94955.361
| Vent Doors | [7 empty] | Back to INDEX
Cost per kg/s Refigerated Air Calculator
|  | Volume of air |  | Fan Inlet Density | 0.96 |  |  |  | c/kWh | 185 | [6 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
|  | Fan Pos | Fan Kg/s | Fan Volume m³/s | Fan Pressure (Pa) | Air Power Wa = | Est. Fan Efficiency % | Fan Ineff kW = | Fan Input Power | Fans Cost / Month |  | Days / Mth |  |  |  | Month | Cost/kWh | Cost/kWh | Cost/kWh | Cost/kWh | Cost/kWh | Cost/kWh
|  | Fan 1 | 0.96 | 1 | 5000 | 5 | 85 | 0.88235 | 5.8824 | 7949.5588 |  | 30.4375 |  |  | 2021 | 2021-01-31 | 0.99625 | 1.1463 | 1.2564 | 1.4908 | 1.6807 | 1.8948
|  | Fan 2 |  | 0 |  | 0 | 85 | 0 | 0 | 0 |  | Sec / Day |  |  |  | 2021-02-01 | 0.98586 | 1.1343 | 1.2433 | 1.4752 | 1.6632 | 1.8751
|  | Fan 3 |  | 0 |  | 0 | 85 | 0 | 0 | 0 |  | 86400 |  |  |  | 2021-03-01 | 0.98811 | 1.1369 | 1.2462 | 1.4786 | 1.667 | 1.8793
|  | Fan 4 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-04-01 | 1.0826 | 1.2456 | 1.3653 | 1.62 | 1.8264 | 2.059
|  | Fan 5 |  | 0 |  | 0 | 85 | 0 | 0 | 0 |  | 95394.7059 |  |  |  | 2021-05-01 | 1.1316 | 1.302 | 1.4271 | 1.6933 | 1.909 | 2.1522
|  | Fan 6 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-06-01 | 1.6273 | 1.8724 | 2.0523 | 2.4351 | 2.7453 | 3.0951
|  | Fan 7 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-07-01 | 1.3424 | 1.5445 | 1.693 | 2.0087 | 2.2646 | 2.5531
|  | Fan 8 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-08-01 | 1.6992 | 1.9551 | 2.1429 | 2.5426 | 2.8665 | 3.2317
|  | Fan 9 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-09-01 | 1.1959 | 1.376 | 1.5082 | 1.7895 | 2.0174 | 2.2745
|  | Fan 10 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-10-01 | 1.1416 | 1.3135 | 1.4398 | 1.7083 | 1.9259 | 2.1713
|  | Fan 11 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-11-01 | 1.1809 | 1.3588 | 1.4894 | 1.7671 | 1.9923 | 2.2461
|  | Fan 12 |  | 0 |  | 0 | 85 | 0 | 0 | 0 | [5 empty] | 2021-12-01 | 1.1073 | 1.2741 | 1.3965 | 1.657 | 1.8681 | 2.1061
|  | Total UG Volume | 0.96 | 1 |  |  |  |  | 5.8824 | 7949.5588 |  |  |  |  | Mean / Average c / kWh |  | 120.6584 | 138.8295 | 152.171 | 180.5509 | 203.5531 | 229.4858
[15 empty] | Increase 5 |  | 15.06% | 9.61% | 18.65% | 12.74% | 12.74% | 1%
|  |  | Fan Kg/s | Fan Volume m³/s | Fan Pressure (Pa) | Air Power Wa = | Est. Fan Efficiency % | Fan Ineff kW = | Fan Input Power | BAC Fans Cost / Month | [6 empty] | 138.8295 | 152.171 | 180.5509 | 203.5531 | 229.4858 | 231.7807
|  | BAC Fan 1 | 1.0417 | 1 | 350 | 0.35 | 75 | 0.11667 | 0.46667 | 630.665
|  | Refrigeration Plants | kW | COP | Absorbed Power | Discount Winter | Mean kW | Refrig. Cost / Month
|  | Plant | 35.5 | 5.5 | 6.4545 | 0.8 | 5.1636 | 6877.9636
|  | Refrigeration Plant PUMPS | kW | Est. Pump Efficiency % | Pump Input Power | Discount Winter | Mean kW | Refrig. Cost / Month
|  | Plant Pumps | 2.2 | 93 | 2.3656 | 0.8 | 1.8925 | 2557.5355
|  | TOTAL Cost / Month |  | 18015.7229 |  | Total cost / mth |  | kW | 13.4051
|  | Cost per Kg/s (Second) |  | 18766.3781 |  | kg/s cost / mth |  | Hr | 24.7995
[8 empty] | Day | 595.1877
|  | Wasted Air (Leakage) |  | 1.2 |  | kg/s |  | Month | 18116.0266
|  |  |  | 22519.6537 |  | per Month |  | Cost / kW /Second | 0.41332
Note on C44: Get this Cost from Eskom website / Costing Dept
Note on C53: Get this Cost from Eskom website / Costing Dept

## PLoss Atkins & Resist
[8 empty] | Back to INDEX | [11 empty] | Velocity in Shaft Calculator |  | 1 | 2 | 3 | 4 | 5
ATKINSON’S FORMULA |  | (Qty) |  |  |  |  | ATKINSON’S FORMULA |  | (Velocity) |  |  |  | ATKINSON’S FORMULA | (Length between two IDENTICAL fans if Qty and Pressure of fans is known) | [6 empty] | Combination | 2 x 6.1mø | 4 x 4.5mø | 2 x 4.5mø + 1 x Alternative | 1 x 4.5mø + 1 x Alternative | 1 x 4.5mø + 1 x Alternative
[13 empty] | Length between fans | [7 empty] | Steady State Qty - m³/s | 450 | 450 | 450 | 450 | 450
P | = | [5 empty] | P | = |  |  |  |  | L | = | [6 empty] | Qty at Shaft 1 - m³/s |  | 287.5 | 349.8 | 469.05 | 469.05
[21 empty] | Qty at Shaft 2 - m³/s |  | 287.5 | 349.8 | Fan off | Fan off
Pipe Diameter = | 5 | m | Enter |  |  |  | Diam. in meters | 0.76 | m | Enter |  |  | Pipe Diameter = | 0.57 | m | Enter |  |  |  |  | Qty at Shaft 3 - m³/s |  | 287.5
L = (in meters) | 1200 | m | Enter |  |  |  | L = (in meters) | 500 | m | Enter |  |  | Presure | 1600 | Pa | Enter |  |  |  |  | Qty Alt shaft - m³/s | 450 | -412.5 | -249.6 | -19.05 | -19.05
Qty (m³/s) | 500 | m³/s | Enter |  |  |  | Velocity (m/s) | 8 | m/s | Enter |  |  | Qty (m³/s) | 5.5 | m³/s | Enter |  |  |  |  | Vent Hole Size - m | 8 | 4.5 | 5.1 | 5.1 | 5.5
w = air density | 1.2 | Kg/m³ | Enter | 1.2 | Kg/m³ |  | w = air density | 0.9 | Kg/m³ | Enter | 1.2 | Kg/m³ | w = air density | 1.2 | Kg/m³ | Enter | 1.2 | Kg/m³ |  |  | Vent Hole Area - m² | 50.2655 | 15.9043 | 20.4282 | 20.4282 | 23.7583
K = | 0.002 | ns²/m⁴ | Enter |  |  |  | K = | 0.0037 | ns²/m⁸ |  |  |  | K = | 0.0037 | ns²/m⁴ | Enter |  |  |  |  | Velocity - m/s | 8.9525 | -25.9364 | -12.2184 | -0.93253 | -0.80183
C = | 15.708 | m |  |  |  |  | C = | 2.3876 | m |  |  |  | C = | 1.7907 | m
A = | 19.635 | m² |  |  |  |  | A = | 0.45365 | m² |  |  |  | A = | 0.25518 | m²
P Drop = | 1245.0347 | Pa |  |  |  |  | P Drop = | 467.3684 | Pa |  |  |  | Length beween fans = | 132.6438 | m |  |  |  |  | Combination | Steady State Qty - m³/s | Qty at Shaft 1 - m³/s | Qty at Shaft 2 - m³/s | Qty at Shaft 3 - m³/s | Qty Alt shaft - m³/s | Vent Hole Size - m | Vent Hole Area - m² | Velocity - m/s | Remarks
R = | 0.0049801 | Ns2/m8 | R = |  |  |  | R = | 35.485 | Ns2/m8 | R = | [8 empty] | 1 | 2 x 6.1mø | 450 | 0 | 0 | 0 | 450 | 8 | 50.2655 | 8.9525 | Ideal
Velocity = | 25.4648 | m/s |  |  |  |  | Loss / m | 0.93474 | Pa/m |  | 861.2 |  | Increse in Pressure loss if a hole size is reduced if partially drilled | [5 empty] | 2 | 4 x 4.5mø | 450 | 287.5 | 287.5 | 287.5 | -412.5 | 4.5 | 15.9043 | -25.9364 | Ideal
Speed = | 91.6732 | km/hr | Loss / m | 1.0375 | Pa/m |  | Qty (m³/s) | 3.6292 | m³/s | [9 empty] | 3 | 2 x 4.5mø + 1 x Alternative | 450 | 349.8 | 349.8 | 0 | -249.6 | 5.1 | 20.4282 | -12.2184 | Ideal
Velocity Pressure = | 389.0733 | Pa |  |  |  |  | ATKINSON’S FORMULA |  | (Velocity) |  |  |  | Qty (m³/s) | 350 |  | m³/s |  |  | 4 | 1 x 4.5mø + 1 x Alternative | 450 | 469.05 | Fan off | 0 | -19.05 | 5.1 | 20.4282 | -0.93253 | Not ideal velocities >30m/s very expensive
ATKINSON’S FORMULA |  | (Qty) | [10 empty] | w = air density | 1.23 |  | Kg/m³ |  |  | 5 | 1 x 4.5mø + 1 x Alternative | 450 | 469.05 | Fan off | 0 | -19.05 | 5.5 | 23.7583 | -0.80183 | Not ideal but can be sustained for short period when one fan is off
P | = | [5 empty] | P | = |  |  |  |  | K Value | 0.007 |  | ns²/m⁴
[13 empty] | Original Hole Length | 445 |  | m |  |  |  | Velocity in Shaft Calculator
L = (in meters) | 400 | m | Enter |  |  |  | L = (in meters) | 0.1 | m | Enter |  |  | Original Hole Diameter | 5.5 |  | m |  |  |  | Intake Shaft | [6 empty] | Expected Air Qty in Shaft |  | 1150 | Number of shafts required | m³/s | Velocity m/s | Mean Velocity m/s
Width (W) | 3 | m | Enter |  |  |  | Width (W) | 0.7 | m | Enter |  |  | Hole leg 1 Length |  | 200 | m |  |  |  | Expected Air Qty |  | 700 | m³/s | Enter |  |  | Shaft |  | Diameter |  | Area (m²)
Height (H) | 3 | m | Enter |  |  |  | Height (H) | 0.7 | m | Enter |  |  | Hole leg 1 Diameter |  | 5.1 | m |  |  |  | Intake Shaft 1 Diameter |  | 7.4 | m | Enter |  |  | Production Shaft |  | 7.4 | 1 | 43.0084 | 26.739 | 9.5845
Qty (m³/s) | 100 | m³/s | Enter |  |  |  | Vel (m/s) | 7 | m/s | Enter |  |  | Hole leg 2 Length |  | 245 | m |  |  |  | Area Shaft 1 = |  | 43.0084 | m² |  |  |  | Service Shaft |  | 9.9 | 1 | 76.9769 | 14.9396
w = air density | 1.117 | Kg/m³ | Enter | 1.2 | Kg/m³ |  | w = air density | 1.4 | Kg/m³ | Enter | 1.2 | Kg/m³ | Hole leg 2 Diameter |  | 4.1 | m |  |  |  | Intake Shaft 2 Diameter |  | 9.9 | m | Enter |  |  | Exploration Shaft |  | 4.7 | 3 | 52.0483 | 22.0948
K = | 0.0121 | ns²/m⁴ | Enter |  |  |  | K = | 0.011 | ns²/m⁸ |  |  |  | Hole leg 3 Length |  |  | m |  |  |  | Area Shaft 2 = |  | 76.9769 | m² |  |  |  | Ventilation Shaft |  | 5.8 | 2 | 52.8416 | 21.7632
C = | 12 | m |  |  |  |  | C = | 2.8 | m |  |  |  | Hole leg 3 Diameter |  |  | m |  |  |  | Intake Shaft 3 Diameter |  |  | m | Enter |  |  | Std 4.5mø Shaft |  | 4.5 | 4 | 63.6173 | 18.0769
A = | 9 | m² |  |  |  |  | A = | 0.49 | m² |  |  |  | Hole leg 4 Length |  |  | m | Ideal velocity |  |  | Area Shaft 3 = |  | 0 | m² |  |  |  | Std 4.8mø Shaft |  | 4.8 | 4 | 72.3823 | 15.8879
P Drop = | 741.6022 | Pa |  |  |  |  | P Drop = | 0.35933 | Pa |  |  |  | Hole leg 4 Diameter |  |  | m | 20 | m/s |  | Ideal Intake shaft velocity |  | 12 | m/s | Enter |  |  | Std 5.1mø Shaft |  | 5.1 | 3 | 61.2846 | 18.7649
R = | 0.07416 | Ns2/m8 | R = |  |  |  | R = | 0.030543 | Ns2/m8 | R = |  |  | Original Hole Pressure Loss | 503.9469 |  | Pa | 14.7317 | m/s |  | Mean Velocity = |  | 5.834 | m/s |  |  |  | Std 5.5mø Shaft |  | 6 | 2 | 56.5487 | 20.3365
Velocity = | 11.1111 | m/s |  |  |  |  | Qty (m³/s) | 3.43 | m³/s |  |  |  | Hole leg 1 - Pressure Loss |  | 330.3827 | Pa | 17.1332 | m/s | [8 empty] | Std 6.5mø Shaft |  | 6.5 | 2 | 66.3661 | 17.3281
Speed = | 40 | km/hr | [10 empty] | Hole leg 2 - Pressure Loss |  | 1205.2719 | Pa | 26.51 | m/s |  | Up-Cast Shaft | [6 empty] | Std 7.0mø Shaft |  | 7 | 1 | 38.4845 | 29.8822
PRESSURE REQUIRED TO OVERCOME FRICTIONAL RESISTANCE | [5 empty] | PRESSURE REQUIRED TO OVERCOME FRICTIONAL RESISTANCE | [6 empty] | Hole leg 3 - Pressure Loss |  | #DIV/0! | Pa | #DIV/0! | m/s |  | Expected Air Qty |  | 550 | m³/s |  |  |  | Std 8.0mø Shaft |  | 8 | 1 | 50.2655 | 22.8785
P = RQ² | [12 empty] | Hole leg 4 - Pressure Loss |  | #DIV/0! | Pa | #DIV/0! | m/s |  | Return Shaft 1 Diameter |  | 3.5 | m | Enter |  |  | Std 9.0mø Shaft |  | 9 | 1 | 63.6173 | 18.0769
[7 empty] | R = | [5 empty] | Additional (E.g.BAC) P.loss | 0 | 0 | Pa |  |  |  | Area Shaft 1 = |  | 9.6211 | m²
Resistance ('R) | 0.037874 | Ns4/m8 | Enter | [9 empty] | Total P.Loss 2 Legs | 503.9469 | 1535.6546 | 1031.7077 | Pa More | Pa More |  | Return Shaft 2 Diameter |  | 3.5 | m | Enter
Qty (m³/s) | 261 | m³/s | Enter |  |  |  | P Drop = | 2580 | Pa | Enter |  |  | Total P.Loss 3 Legs | 503.9469 | #DIV/0! | #DIV/0! | #DIV/0! | Pa Less |  | Area Shaft 2 = |  | 9.6211 | m²
P Drop = | 2580 | Pa |  |  |  |  | Qty (m³/s) | 261 | m³/s | Enter |  |  | Total P.Loss 4 Legs | 503.9469 | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Return Shaft 3 Diameter |  | 3.5 | m | Enter
SHOCK LOSS CALC (Bend) | [6 empty] | Resistance ('R) | 0.037874 | Ns2/m8 | [10 empty] | Area Shaft 3 = |  | 9.6211 | m²
[13 empty] | Original Hole Velocity | 14.7317 | m/s |  |  |  |  | Return Shaft 4 Diameter |  |  | m | Enter
ΔP = | K*½wv² |  |  | R/D Ratio | K Factor (Approx) | [7 empty] | Hole 1 Velocity | 17.1332 | m/s |  |  |  |  | Area Shaft 4 = |  | 0 | m²
w = air density | 1.2 | Kg/m³ | Enter | 0.5 | 0.9 | [7 empty] | Hole 2 Velocity | 26.51 | m/s |  |  |  |  | Water Blanket lower shaft velocity |  | 7 | m/s
v = air velocity | 20 | m/s | Enter | 1 | 0.33 | [7 empty] | Hole 3 Velocity | #DIV/0! | m/s |  |  |  |  | Water Blanket upper shaft velocity |  | 13 | m/s
Dimensionless loss coefficient (K) | 0.9 | * | Enter | 1.5 | 0.24 |  | P Drop = | 2580 | Pa | Enter |  |  | Hole 4 Velocity | #DIV/0! | m/s |  |  |  |  | Economical Velocity |  | 22.04 | m/s | Enter
ΔP Pressure loss = | 216 | Pa | Enter | 2 | 0.19 |  | Resistance ('R) | 0.037874 | Ns2/m8 | Enter | [9 empty] | Mean Velocity = |  | 19.0553 | m/s
[7 empty] | Qty (m³/s) | 261 | m³/s | m³/s
AIR POWER | [20 empty] | Shock loss Calculator | 2.7 | 2.4 | 1.8 | 1.4 | 1.8 | 2.79
| Wa = |  |  |  | OR |  | Wa = | [5 empty] | ATKINSON’S FORMULA - Quick Calc |  | (Qty) | [6 empty] | 8 | 6 | 5 | 4.7 | 4.5 | 3
[13 empty] | P | = | [6 empty] | c/kWh | 185 | c
[21 empty] | 1.2 | Kg/m³
Pressure (P) | 2700 | Pa | Enter |  |  |  | Resistance ('R) | 0.0194 | Ns4/m8 | Enter |  |  | Shaft Diameter = | 5.5 | m | Enter |  |  |  |  | Pipe Diameter = (m) | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Qty (m³/s) | 35 | m³/s | Enter |  |  |  | Qty (m³/s) | 176 | m³/s | Enter |  |  | L = (in meters) | 2500 | m | Enter |  |  |  |  | L = (in meters) | 200 | 200 | 200 | 200 | 200 | 200
Wa = | 94.5 | kW |  |  |  |  | Wa = | 105.7645 | kW |  |  |  | Qty (m³/s) | 300 | m³/s | Enter |  |  |  |  | Qty (m³/s) | 82 | 82 | 82 | 82 | 82 | 82
Wa = | 0.0945 | MW |  |  |  |  | Wa = | 0.10576 | MW |  |  |  | w = air density | 1.3 | Kg/m³ | Enter | 1.2 | Kg/m³ |  |  | w = air density (Kg/m³) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
[13 empty] | K = | 0.004 | ns²/m⁴ | Enter |  |  |  |  | K = ns²/m⁴ | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
VELOCITY PRESSURE | [6 empty] | Motor input power | [5 empty] | C = | 17.2788 | m | [5 empty] | C = (m) | 7.5398 | 7.5398 | 7.5398 | 7.5398 | 7.5398 | 7.5398
| 24.7207 | [6 empty] | W= |  |  |  |  | A = | 23.7583 | m² | [5 empty] | A = (m²) | 4.5239 | 4.5239 | 4.5239 | 4.5239 | 4.5239 | 4.5239
VP = | [12 empty] | P Drop = | 1256.2365 | Pa | [5 empty] | P Drop = (Pa) | 438.9808 | 438.9808 | 438.9808 | 438.9808 | 438.9808 | 438.9808
[7 empty] | Voltage [kV] | 11.346 | kV | Enter |  |  | Intake Shaft P.Loss | 150 | Pa | [5 empty] | R = (Ns2/m8) | 0.065286 | 0.065286 | 0.065286 | 0.065286 | 0.065286 | 0.065286
v = air velocity | 24.7 | [m/s] | Enter |  |  |  | Current [amperes] | 186.3 | A | Enter |  |  | Tunnels P.Loss | 2000 | Pa | [5 empty] | Velocity = (m/s) | 18.126 | 18.126 | 18.126 | 18.126 | 18.126 | 18.126
w = air density | 1.099 | [kg/m³] | Enter |  |  |  | Power factor | 0.9778 |  | Enter |  |  | Total Pressure Loss | 3406.2365 | Pa | [5 empty] | Speed = (km/h) | 65.2535 | 65.2535 | 65.2535 | 65.2535 | 65.2535 | 65.2535
VP = | 335.2445 | Pa | velocity pressure [Pa] |  |  |  | Number of phases | 3 |  | Enter | [10 empty] | Velocity Pressure (Pa) | 213.5582 | 213.5582 | 213.5582 | 213.5582 | 213.5582 | 213.5582
[7 empty] | Electric power | 3579.8621 | kW | [11 empty] | Shock Loss Factor (If Known) | 1 | 1 | 1 | 1 | 1 | 1
[13 empty] | ATKINSON’S FORMULA - Qty Calc |  | (Qty) | [5 empty] | ∆Velocity Pressure (Pa) | - | 0 | 0 | 0 | 0 | 0
DARCY-WEISBACH EQUATION | [6 empty] | Motor output power | [13 empty] | Wa = (kW) | 35.9964 | 35.9964 | 35.9964 | 35.9964 | 35.9964 | 35.9964
[8 empty] | W= |  |  |  |  | Q = | P. A3 x 1.2 | [6 empty] | Cost / Month | 47947.2417 | 47947.2417 | 47947.2417 | 47947.2417 | 47947.2417 | 47947.2417
P | = | [12 empty] | KCL w | [6 empty] | Fan Efficiency (%) | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
[7 empty] | Voltage [kV] | 11.1 | kV | Enter | [10 empty] | TOTAL Cost / Month | 55111.772 | 55111.772 | 55111.772 | 55111.772 | 55111.772 | 55111.772
L = (in meters) | 18400 | m | Enter |  |  |  | Current [amperes] | 186 | A | Enter |  |  | Pipe Diameter = | 1.4 | m | Enter |  |  |  |  | TOTAL Cost / Annum | 661341.2645 | 661341.2645 | 661341.2645 | 661341.2645 | 661341.2645 | 661341.2645
w = air density | 0.9 | [kg/m³] | Enter | 1.2 | Kg/m³ |  | Power factor | 0.98 | pf | Enter |  |  | L = (in meters) | 600 | m | Enter
v = air velocity | 13.55 | [m/s] | Enter |  |  |  | Number of phases | 3 |  | Enter |  |  | P Drop = | 2000 | Pa | Enter |  |  |  |  | Velocity Pressure Cost per section | 0 | 0 | 0 | 0 | 0 | 0
Diam. in meters | 1.3 | m | Enter |  |  |  | Motor efficiency | 0.95 | % | Enter |  |  | w = air density | 1.3 | Kg/m³ | Enter | 1.2 | Kg/m³ |  |  | Cumulative Velocity Pressure Cost | 0 | 0 | 0 | 0 | 0 | 0
l µ density | 0.009 | Factor |  |  |  |  | Electric power | 3329.2486 | kW |  |  |  | K = | 0.004 | ns²/m⁴ | Enter
l = | 0.012 | Factor | [10 empty] | C = | 4.3982 | m | [5 empty] | Velocity | Water Blanket
P = | 10524.6602 | Pa | [10 empty] | A = | 1.5394 | m² | [6 empty] | Hole uneconomical
[13 empty] | Qty (m³/s) | 25.2585 | m³/s | [6 empty] | Good
REGULATORS | [6 empty] | K Factors | [14 empty] | Costly
[7 empty] | Smooth concrete lined shafts - rope guide |  |  | 0.03 | ns²/m⁴ | 0.02 | [9 empty] | Very Costly
Ar =1.2Q | Or, when the air density is 1.2 kg/m3 |  |  | Ar = |  |  | Smooth concrete lined shafts |  |  | 0.007 | ns²/m⁴ | [10 empty] | Extremely Costly
[7 empty] | Smooth concrete lined shafts - No steel |  |  | 0.004 | ns²/m⁴ |  | ATKINSON’S FORMULA - Qty Calc |  | (Qty) | [5 empty] | Note: This is an indicative calulator calculating the shockloss due to change in duct size and to select most economical hole size
Qty (m³/s) | 28 | m³/s | Enter |  |  |  | Smooth concrete lined shafts - RSJ Buntons |  |  | 0.03375 | ns²/m⁴
p = pressure used up by regulator | 1000 | [Pa] | Enter |  |  |  | Smooth concrete lined shafts - Streamlined Buntons |  |  | 0.014 | ns²/m⁴ |  | Q = | P. A3 x 1.2
w = air density | 1.12 | [kg/m³] | Enter |  |  |  | Smooth Raise bore / concrete shafts |  |  | 0.0037 | ns²/m⁴ |  |  | KCL w
Ar = | 1.1245 | m² |  |  |  |  | Unlined Raise bore shaft |  |  | 0.008 | ns²/m⁴ | [8 empty] | Mentis Grating open area Calc
Ar = | 1.1599 | m² | Desity = 1.2kg/m³ |  |  |  | Unlined Shafts and Tunnels - Uniform Sidewall |  |  | 0.012 | ns²/m⁴ |  | Width (W) | 6 | m | Enter
Calculated Regulator Size Rectangular / Square | [6 empty] | Unlined Shafts and Tunnels - Irregular Sidewall |  |  | 0.016 | ns²/m⁴ |  | Height (H) | 6 | m | Enter
Width | 1 | m |  |  |  |  | Sinking Duct |  |  | 0.0025 | ns²/m⁴ |  | L = (in meters) | 1200 | m | Enter |  |  |  | Type of Mentis Grating | Cross bar "Width" | 40 | mm
Calculated Height | 1.1245 | m |  |  |  |  | 6 Swage standard galvanized Vent Duct |  |  | 0.0037 | ns²/m⁴ |  | P Drop = | 2407.4 | Pa | Enter |  |  |  |  | Bearing Bar "Length" | 40 | mm
[7 empty] | Flexible Ducting |  |  | 0.003 | ns²/m⁴ |  | w = air density | 1.117 | Kg/m³ | Enter | 1.2 | Kg/m³ |  |  | Cross bar Thickness (Typical 8,5mm) | 8.5 | mm
Width | 1000 | mm |  |  |  |  | Flexible Ducting Spiral Support |  |  | 0.0055 | ns²/m⁴ |  | K = | 0.01 | ns²/m⁴ | Enter |  |  |  |  | Bearing Bar Thickness (Typical 4,0mm) | 4 | mm
Calculated Height | 1124.4711 | mm | [10 empty] | C = | 24 | m |  |  |  |  | 1m x 1m (mm² and m²) | Number of open Gaps Cross bar "Width" | 25 | Count 1m Width
[13 empty] | A = | 36 | m² |  |  |  |  | 1000000 | Number of open Gaps Bearing Bar "Length" | 25 | Count 1m Length
Calculated Regulator Size Round | [12 empty] | Qty (m³/s) | 647.2852 | m³/s |  |  |  |  | 1000 | Number of open holes per m² | 625 | Count
Calculated Dia. | 1.1965 | m | [10 empty] | Velocity | 17.9801 | m/s | [5 empty] | Cross bar Open gap | 31.5 | mm
Calculated Dia. | 1196.5455 | mm | [18 empty] | Bearing Bar Gap | 36 | mm
[7 empty] | Vent Hole Dimension Calculator | [5 empty] | Engine capacity to Volume | [7 empty] | Open Area mm² | 1134 | mm²
Velocity | 24.9006 | m/s | [18 empty] | Open Area m² | 708.75 | m²
[7 empty] | v = Max Air velocity |  | 20 | m/s | Enter |  | Engine Capacity | 6.7 | L | Enter |  |  |  |  | % Restriction / Area reduction | 29.125 | % | 29.12%
[7 empty] | Airflow Required |  | 150 | m³/s | Enter |  | Engine Capacity m³ | 0.0067 | m³ | [5 empty] | % Open Area | 70.875 | %
[7 empty] | A = |  | 7.5 | m² |  |  | Revolutions per min | 2200 | rpm | Enter |  |  |  |  | Hole Diameter = | 4.5 | m | Enter
[13 empty] | Revolutions per sec | 36.6667 | rpsec | [5 empty] | C = | 14.1372 | m
[7 empty] | Round |  | 3.0902 | m ø |  |  | Air Displacement m³/s | 0.24567 | m³/s | [5 empty] | A = Open | 15.9043 | m²
[21 empty] | A = Open Mentis Grating | 11.2722 | m²
[7 empty] | Square | H = | 2.5 | m | Enter
Pressure (P1) | 4500 | Pa | Enter |  |  |  |  | W = | 3 | m
Qty 1 (m³/s) | 319 | m³/s | Enter
Qty 1 (m³/s) | 443 | m³/s | Enter
P2 = | 8678.3788 | Pa
P2 = | 8.6784 | kPa
Velocity Pressure Manupulation
Atkinson's Manupulation
Note on H42: Sharp Bend
Note on H43: Standard Radius
Note on E44: * - Dimensionless loss coefficient (See Table)
Note on H44: Long Radius
Note on H45: Smooth Transition Bend
Note on Z51: NOTEt: Change Value on Cost Tab: =Cost!C33
Note on Q61: Drift Losses etc...
Note on Z65: Johan van Sittert: Use "1" if unknown
Note on AA65: Johan van Sittert: Use "1" if unknown
Note on AB65: Johan van Sittert: Use "1" if unknown
Note on AC65: Johan van Sittert: Use "1" if unknown
Note on AD65: Johan van Sittert: Use "1" if unknown
Note on AE65: Johan van Sittert: Use "1" if unknown
Note on Z91: NOTE: The Build up / Fouling of dust or material can be measured and entered as a "thickness" value to calculate % restriction
Note on Z92: NOTE: The Build up of dust / material can be measured and entered as a thickness value to calculate % restriction

## Stope Calcs
Back to INDEX
AUI Calc - Old "Easy Calc" | [5 empty] | AUI Calc - "Design Qty Calc" |  |  |  | "#1" AIR UTILIZATION INDEX (AUI%)
Parameters | ENTER |  |  |  |  | Parameters | ENTER |  |  | SINGLE SIDED | ENTER |  |  | DOUBLE SIDED | ENTER
Available Qty m³/s | 14 | m³/s |  |  |  | Available Qty m³/s | 14 | m³/s |  | Available Quantity | 14 | m³/s |  | Available Quantity | 14 | m³/s
Average Stoping width m | 0.85 | m |  |  |  | Design Qty m³/s | 12 | m³/s |  | Average face velocity | 0.5 | m/s |  | Average face velocity | 0.5 | m/s
Average Vent Control distance m | 4.5 | m |  |  |  | Target Velocity @ 80% leakage | 0.93333 | m/s |  | Average Vent Control distance m | 4.5 | m |  | Average Vent Control distance m | 9 | m
Average Actual velocity m/s | 0.5 | m/s | [7 empty] | Average Stoping width | 1.4 | m |  | Average Stoping width | 1.4 | m
[6 empty] | Average Actual velocity m/s | 0.5 | m/s
| Single Side Stope |  | Double Side Stope | [6 empty] | AIR UTILIZATION | 25.2 | % |  | AIR UTILIZATION | 50.4 | %
Potential vel. m/s with 20% leakage | 2.9281 | m/s | 1.4641 | m/s |  |  | Single and Double Side Stope
Air Utilization | 17.0759 | % | 34.1518 | % |  | Air Utilization | 53.5714 | % |  | NOTE
[10 empty] | LEDGING STOPES |  | - | NO AUI VALUE !!!
AUI Calc taking C/Gully vel into consideration | [5 empty] | AUI Calc - "Simple Design Velocity Calc" |  |  |  | VAMPING STOPES |  | - | NO AUI VALUE !!!
Parameters | ENTER |  |  |  |  | Parameters | ENTER
Available Qty m³/s Stope Intake | 14 | m³/s |  |  |  | Design Velocity | 1 | m/s
Average Stoping width m | 1.4 | m |  |  |  | Average Actual velocity m/s | 0.5 | m/s
Average Vent Control distance m | 4.5 | m
Average Actual velocity m/s | 0.5 | m/s
C/Gully Vel | 0 | m/s |  |  |  |  | Single and Double Side Stope
C/Gully Width | 1.2 | m |  |  |  | Air Utilization | 50 | %
C/Gully height | 2.7 | m
C/Gully Qty | 0 | m³/s
Available Qty m³/s Stope Intake | 14 | m³/s
| Single Side Stope |  | Double Side Stope
Potential vel. m/s with 20% leakage | 1.7778 | m/s | 0.88889 | m/s
Air Utilization | 28.125 | % | 56.25 | %
AUI Calc taking Strike (Stope Span) Distance into consideration
| AUI = | AVE. ACTUAL VELOCITY |  |  | X 100
|  | POTENTIAL VELOCITY |  |  | 1
| AVE. POTENTIAL VELOCITY = |  |  |  | AVAILABLE AIR VOLUME |  |  | 14 | m³/s
[5 empty] | S - SC X 0.00185+ 1 X SW X SC |  |  | 6.9469 | m³/s
WHERE : | S = AVERAGE STOPING SPAN ( m )
SC = STANDARD STRIKE CONTROL ( 18,0 m FOR DOUBLE SIDED AND 9.0 m FOR SINGLE SIDED )
SW = AVERAGE STOPING HEIGHT ( m )
VARIABLES : | AVAIL. AIR VOLUME : |  |  | 14
| AVE. STOPE SPAN : |  |  | 60
| STD. STRIKE CONTROL : |  |  | 4.5
| STOPING WIDTH : |  |  | 1.4
| AVE ACTUAL VEL : |  |  | 0.5
| POTENTIAL VELOCITY : |  |  | 2.0153 | m/s
|  |  | AUI : | 24.8102 | %

## Dev Calcs
Back to INDEX
Leakage |  |  |  | Disch Qty Required (Quick Calc) |  |  |  | Pipe Quantities
Parameters | ENTER |  |  | Parameters |  |  |  | Parameters
Qty in m³/s | 24.12 |  |  | Fan Intake Qty in m³/s | 8.3 | m³/s |  | Velocity fan Intake m/s | 19.8 | m/s
Qty out m³/s | 14.5 |  | 280.0001 | Expected % Leakage of the column | 10 | %/100m |  | Pipe Size in mm | 1500 | mm
Length of collumn m | 280 |  | 279.9999 | Expected TOTAL Leakage over distance | 50 | %/100m |  | Pipe size in m | 1.5 | m
TOTAL Leakage | 39.8839 | % |  | Length of collumn in meters | 500 | m |  | Pipe Area | 1.7671 | m²
Leakage if Column is < 100m long | 0 | %/100m |  | Expected Discharge Qty m³/s | 4.15 | m³/s |  | Qty m³/s | 34.9895 | m³/s
Leakage if Column is > 100m long | 14.2442 | %/100m
Tunnel Quantities
[6 empty] | ENTER |  | Parameters
|  | ENTER |  | PRESSURE LOSS CALC | Qty | 100 | m³/s | Velocity m/s | 3.5 | m/s
PRESSURE LOSS CALC | Qty | 450 | m³/s | For a V.Hole | Diam.(m) | 3 | m | Tunnel height in m | 0.7 | m
For a Pipe | Diam.(m) | 8.5 | m |  | Length (m) | 180 | m | Tunnel width in m | 2.55 | m
| Length (m) | 300 | m |  | K-Factor | 0.004 | ns²/m4 | Tunnel Area | 1.785 | m²
| K-Factor | 0.002 | ns²/m4 |  | Density | 1.3 | Kg/m³ | Qty m³/s | 6.2475 | m³/s
| Density | 1.26 | Kg/m³ |  | Circumference | 9.4248 | m
| Circumference | 26.7035 | m |  | Area | 7.0686 | m²
| Area | 56.745 | m² | PRESSURE LOSS = |  | 208.1462 | Pa
PRESSURE LOSS = |  | 18.6445 | Pa | Velocity in Vent Hole |  | 14.1471 | m/s
|  | 7.9302 | m/s
ENTER
|  | ENTER |  | PRESSURE LOSS CALC | Qty | 10 | m³/s
PRESSURE LOSS CALC | Qty | 510 | m³/s | For Square Duct | Height (m) | 0.5 | m
For a Tunnel | Height (m) | 5.44 | m |  | Width (m) | 1.62 | m
| Width (m) | 5 | m |  | Length (m) | 76 | m
| Length (m) | 407 | m |  | K-Factor | 0.0024 | ns²/m4
| K-Factor | 0.011 | ns²/m4 |  | Density | 1.26 | Kg/m³
| Density | 1.26 | Kg/m³ |  | Circumference | 4.24 | m
| Circumference | 20.88 | m |  | Area | 0.81 | m²
| Area | 27.2 | m² | PRESSURE LOSS = |  | 152.8006 | Pa
PRESSURE LOSS = |  | 1268.6462 | Pa
K Factors
6 Swage standard gavanized Duct | 0.0037 | ns²/m4
Mild Steel smooth Bore vent Duct (Sinking Duct) | 0.00275 | ns²/m4
K Factor on Smooth bore pipes | 0.002 | ns²/m4
LHPC Ducting Type A | 0.0015 | ns²/m4
LHPC Ducting Type B | 0.002 | ns²/m4
Note on E5: Van Sittert, Johan: Note hidden formulae To be able to calculate >200m
Note on E6: Van Sittert, Johan: Note hidden formulae To be able to calculate >200m
Note on D9: Van Sittert, Johan: Percentage Leakage per 100m

## Dev Qtys
Back to INDEX
| Air Qty Required to meet (Std) Conventional |  |  |  | Fan KW | Fan Qty m³/s |  |  | Qty Decrease over Distance |  |  |  | Primary Fan requirement to cater for a 2'nd fan - Calculator | [9 empty] | Qty based on End Dimension |  |  |  | Qty based on Diesel Machine
| Parameters | [7 empty] | 100 | [11 empty] | End B |  | W = | 5.5 | m |  | kW | 220 | kW
| Required Face Minimum Qty in m³/s/m² | 0.2 | m³/s/m² |  | 2.2 | 1.5 | m³/s | 3.2 | 100 | 4.05 | m³/s |  |  |  | Overlap Fan 1 based on End Dimension | [7 empty] | H = | 6 | m |  | Dilution Std | 0.06 | m³/s/kW
| End Width | 3.5 | m |  | 4 | 3.2 | m³/s | 4.5 | 200 | 3.645 | m³/s |  |  |  | W = | 5.5 | m | [5 empty] | Area | 33 | m³/s/m² |  | Area | 13.2 | m³/s/kW
| End Height | 3.5 | m |  | 7.5-8.0 | 4.5 | m³/s | 6 | 300 | 3.2805 | m³/s |  | Main Available Air Requirement |  | H = | 6 | m | [5 empty] | Airflow Std | 0.5 | m³/s/m²
| Length of collumn in meters | 250 | m |  | 11.0-15.0 | 6 | m³/s | 7.5 | 400 | 2.9524 | m³/s |  |  |  | Area | 33 | m³/s/m² | [5 empty] | Qty Req | 16.5 | m³/s
| % Leakage of the column | 10% | /100m |  | 18.0-18.5 | 7.5 | m³/s | 9 | 500 | 2.6572 | m³/s |  | 63 | m³/s | Overlap Airflow Std | 0.5 | m³/s/m²
| End Face Area | 12.25 | m² |  | 22 | 9 | m³/s | 12.5 | 600 | 2.3915 | m³/s |  |  |  | Qty Req | 16.5 | m³/s | [5 empty] | End B Final Distance | 200 | m
| Qty of Air required on Face | 2.45 | m³/s |  | 37.5-45.0 | 12.5 | m³/s | 18.5 | 700 | 2.1523 | m³/s | [11 empty] | End B Face Qty Req. | 16.5 | m³/s
| Expected Leakage over distance "Total" | 25 | % |  | 75 | 18.5 | m³/s | 40 | 800 | 1.9371 | m³/s | [11 empty] | End B Fan Qty Req. | 21.45 | m³/s
| Overlap velocity Required at fan | 0.3 | m/s |  | 160 | 40 | m³/s | 40 | 900 | 1.7434 | m³/s
| Overlap end Width at fan | 4.5 | m | [5 empty] | 1000 | 1.5691 | m³/s
| Overlap end Height at fan | 4.5 | m | [5 empty] | 1100 | 1.4121 | m³/s
| Overlap Qty Required at fan | 6.075 | m³/s | [5 empty] | 1200 | 1.2709 | m³/s |  |  |  | Overlap | [7 empty] | Fan 2 |  |  |  |  | End A
| Expected Required fan Qty over distance | 3.0625 | m³/s | [5 empty] | 1300 | 1.1438 | m³/s | [10 empty] | Overlap
| Calculated Required Qty m³/s for end | 9.1375 | m³/s | [5 empty] | 1400 | 1.0295 | m³/s
| Closest fan to met delivery Qty | 4.5 | m³/s | [5 empty] | 1500 | 0.92651 | m³/s
| Actual Required Qty for End before fan | 10.575 | m³/s
| Expected Delivery Qty m³/s on Face | 3.645 | m³/s | Note if this is red - increase Minimum fan Qty until black (That will be the minmum fan intake Qty required) | [10 empty] | Fan 1 | [7 empty] | Fan 2 | 1 | 1 = Yes 0 = No
[23 empty] | Distance from Fan 1 | 200 | m | … or End A Max Length
[18 empty] | Overlap Fan 2 based on End Dimension |  |  |  |  | Leakage Fan 2 | 15% | %/100m
| Air Qty Required to meet (Std) Trackless | [7 empty] | Qty Decrease over Distance | [8 empty] | W = | 5.5 | m |  |  | Fan 2 Column Leakage | 30 | % Total Leakage
| Parameters | [7 empty] | 100 | [8 empty] | H = | 6 | m |  |  | Fan 2 Qty Requirement | 37.95 | m³/s | … or End A Qty Requirement
| Tracless Vehicle kW | 144 | kW | [5 empty] | 100 | 11.875 | m³/s | [6 empty] | Area | 33 | m³/s/m²
| Disel Dilution Criteria | 0.063 | m3/s per kW rated diesel power | [5 empty] | 200 | 11.2812 | m³/s | [6 empty] | Overlap Airflow Std | 0.5 | m³/s/m²
| Required Face Minimum Qty in m³/s/m² | 0.3024 | m³/s/m² | [5 empty] | 300 | 10.7172 | m³/s |  | Fan 1 |  |  |  |  | Qty Req | 16.5 | m³/s
| Diesel Equipment Air requirement | 9.072 | m³/s | [5 empty] | 400 | 10.1813 | m³/s |  | End 2 Distance to Fan 2 | 200 | m
| End Width | 6 | m |  | Fan KW | Est. Fan Qty m³/s |  |  | 500 | 9.6723 | m³/s |  | End 1 Qty Req. at Fan 2 | 37.95 | m³/s
| End Height | 5 | m | [5 empty] | 600 | 9.1886 | m³/s |  | Leakage Fan 1 | 10% | %/100m
| Length of collumn in meters | 300 | m |  | 22 | 8.9796 | m³/s | 12.5 | 700 | 8.7292 | m³/s |  | Fan 1 Column Leakage | 20 | % Total Leakage
| % Leakage of the column | 5% | /100m |  | 37.5-45.0 | 12.5 | m³/s | 25 | 800 | 8.2928 | m³/s |  | Fan 1 Fan Qty Req. | 45.54 | m³/s
| End Face Area | 30 | m² |  | 75 | 25 | m³/s | 33.3333 | 900 | 7.8781 | m³/s
| Qty of Air required on Face | 9.072 | m³/s |  | 100 | 33.3333 | m³/s | 52 | 1000 | 7.4842 | m³/s
| Expected Leakage over distance (Total Leakage) | 15 | % |  | 130 | 52 | m³/s | 60 | 1100 | 7.11 | m³/s
| Overlap velocity Required at fan | 0.3 | m/s |  | 150 | 60 | m³/s | 76.1905 | 1200 | 6.7545 | m³/s
| Overlap end Width at fan | 5 | m |  | 160 | 76.1905 | m³/s | 85.7143 | 1300 | 6.4168 | m³/s
| Overlap end Height at fan | 5 | m |  | 180 | 85.7143 | m³/s | 90.4762 | 1400 | 6.0959 | m³/s
| Overlap Qty Required at fan | 7.5 | m³/s |  | 190 | 90.4762 | m³/s | 90.4762 | 1500 | 5.7911 | m³/s
| Expected Required fan Qty over distance | 10.4328 | m³/s
| Calculated Required Qty m³/s for end | 17.9328 | m³/s
| Closest fan to met delivery Qty | 12.5 | m³/s
| Actual Required Qty for End before fan | 20 | m³/s
| Expected Delivery Qty m³/s on Face | 10.7172 | m³/s | Note if this is red - increase Minimum fan Qty until black (That will be the minmum fan intake Qty required)
Back to INDEX
| Air Qty Required to meet (Std - Shaft Sinking) Conventional |  |  |  | Fan KW | Fan Qty m³/s |  |  | Qty Decrease over Distance
| Parameters | [7 empty] | 100
Force Column | Required Face Minimum Qty in m³/s/m² | 0.25 | m³/s/m² |  | 750 | 36.5854 | m³/s | 39.0244 | 100 | #N/A | m³/s | 36.5854
| Shaft Diameter | 7 | m |  | 800 | 39.0244 | m³/s | 41.4634 | 200 | #N/A | m³/s | 39.0244
| Shaft Lining | 0.3 | m |  | 850 | 41.4634 | m³/s | 43.9024 | 300 | #N/A | m³/s | 41.4634
| C = | 21.9911 | m |  | 900 | 43.9024 | m³/s | 46.3415 | 400 | #N/A | m³/s | 43.9024
| Length of collumn in meters | 18 | m |  | 950 | 46.3415 | m³/s | 48.7805 | 500 | #N/A | m³/s | 46.3415
| % Leakage of the column | 1.1% | /100m |  | 1000 | 48.7805 | m³/s | 51.2195 | 600 | #N/A | m³/s | 48.7805
| Shaft Face Area | 38.4845 | m² |  | 1050 | 51.2195 | m³/s | 53.6585 | 700 | #N/A | m³/s | 51.2195
| Qty of Air required on Face | 9.6211 | m³/s |  | 1100 | 53.6585 | m³/s | 56.0976 | 800 | #N/A | m³/s | 53.6585
| Expected Leakage over distance "Total" | 0.198 | % |  | 1150 | 56.0976 | m³/s | 56.0976 | 900 | #N/A | m³/s | 56.0976
Exhaust Column | Length of Exhaust collumn in meters | 1200 | m | [5 empty] | 1000 | #N/A | m³/s | 0
| Overlap velocity Required at fan | 0.5 | m/s | [5 empty] | 1100 | #N/A | m³/s
| % Leakage of the Exhaust column | 1.1% | /100m | [5 empty] | 1200 | #N/A | m³/s
| Qty lost due to density | 0.9 | m³/s | [5 empty] | 1300 | #N/A | m³/s
| 4 Gate or system Leakage | 1 | m³/s | [5 empty] | 1400 | #N/A | m³/s
| Overlap Area at fan | 35.2565 | m² |  | Max at Overlap |  |  |  | 1500 | #N/A | m³/s
| C = | 21.9911 | m |  | 20
| Expected Leakage over distance "Total" | 13.002 | %
| Overlap Qty Required at Force fan Velocity at 0.5m/s | 17.6283 | m³/s |  | 1
| Overlap Qty Required 2 X Force fan Quantity | 20 | m³/s
| Force fan Qty REQUIRED | 9.6402 | m³/s |  | Leakage Force | 0.01905 | m³/s
| Exhaust Qty REQUIRED | 31.5402 | m³/s
| Calculated Exhaust Fan Qty m³/s for Shaft | 35.641 | m³/s |  | Leakage Exhaust | 4.1009 | m³/s
| Closest fan to met delivery Qty | #N/A | m³/s
| Actual Required Qty for force fan | 35.641 | m³/s
| Expected Delivery Qty m³/s on Face - Fan | #N/A | m³/s | Note if this is red - increase Minimum fan Qty until black (That will be the minmum fan intake Qty required)
Note on C3: Van Sittert, Johan: This is a tool to help calc what the delivery Qty could be if you enter some random parameters to show the mining guys what must be done to get a certain amount of air on the face (If you have some actual figures it helps you to prove your point – by reducing leakage you can work out how far it could be possible to develop)
Note on AN4: Johan van Sittert: If no Diesel units are used, make this value a "0"
Note on L5: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L6: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L7: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L8: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L9: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on X9: Johan van Sittert: If Fan is installed in a wall make this value a "0"
Note on L10: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L11: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L12: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L13: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L14: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L15: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L16: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L17: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L18: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L19: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L26: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L27: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L28: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L29: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L30: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L31: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L32: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L33: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L34: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L35: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L36: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L37: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L38: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L39: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L40: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on C50: Van Sittert, Johan: This is a tool to help calc what the delivery Qty could be if you enter some random parameters to show the mining guys what must be done to get a certain amount of air on the face (If you have some actual figures it helps you to prove your point – by reducing leakage you can work out how far it could be possible to develop)
Note on L52: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on O52: Johan van Sittert: 20.5 "Factor" to devide kW to get Qty delivered for Shaft sinking high pressure fans
Note on L53: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L54: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L55: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on D56: Johan van Sittert: If is only an exhaust system enter "0"
Note on L56: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L57: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L58: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L59: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L60: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L61: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on D62: Johan van Sittert: If is only an exhaust system enter "0"
Note on L62: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L63: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L64: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L65: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement
Note on L66: Johan van Sittert:Note if value is bold and red the quantity does'nt meet the minimum requirement

## Interpolation
Interpolation | [5 empty] | Back to INDEX
[12 empty] | 20 | 30 | 38 | 40 | Degrees setting
[11 empty] | P | Qty | Qty | Qty | Qty
Value A | 3 | = | -0.12 | Value X |  | Value A | 800 | = | 42.2 | Value X | 6000 | 235 | 192 | 157.6 | 149
Value B | 4.25 | = | -0.17625 | Value Y |  | Value B | 1000 | = | 46.2 | Value Y | 5500 | 266 | 230 | 201.2 | 194
Value C | 5 | = | -0.21 | Value Z |  | Value C | 900 | = | 44.2 | Value Z | 5000 | 293 | 258 | 230 | 223
[11 empty] | 4500 | 318 | 280 | 249.6 | 242
The formula is thus: | [6 empty] | Quick Copy and Paste Data |  |  |  | 4000 | 344 | 305 | 273.8 | 266
[6 empty] | Value set A | 800 | 42.2 |  |  | 3500 | 365 | 326 | 294.8 | 287
[6 empty] | Value set C | 900 | 44.2 |  |  | 3000 | 380 | 345 | 317 | 310
[6 empty] | Value set B | 1000 | 46.2 | Value Y |  | 2500 | 398 | 361 | 331.4 | 324
[11 empty] | 2000 | 410 | 375 | 347 | 340
[11 empty] | 1500 | 422 | 388 | 360.8 | 354
[11 empty] | 1000 | 435 | 398 | 368.4 | 361
[5 empty] | Interpolation Multiple data Points | [5 empty] | 500 | 445 | 412 | 385.6 | 379
[11 empty] | 0 | 455 | 419 | 390.2 | 383
[6 empty] | Value A | 3 | = | -0.12
[6 empty] | Value B1 | 3.25 | = | -0.13125
[6 empty] | Value B2 | 3.5 | = | -0.1425
[6 empty] | Value B3 | 3.75 | = | -0.15375
[6 empty] | Value B4 | 4 | = | -0.165
[6 empty] | Value B5 | 4.25 | = | -0.17625
[6 empty] | Value B6 | 4.5 | = | -0.1875
[6 empty] | Value B7 | 4.75 | = | -0.19875
[6 empty] | Value C | 5 | = | -0.21

## Dust
Back to INDEX
FORMULAE TO WORK OUT NUMBER OF FILTER BAGS REQUIRED
Number of bags required :
1) Area of tip x velocity down tip ( 0.5 m/s )=Volume down tip
2) Surface area of one bag x velocity through one bag ( 0.1 m/s ) = Volume through one bag
3) Volume down tip / Volume though one bag = Amount of bags required
Surface area of one bag = ( pie x D x L ) + ( pie x r² )
Area of tip |  | 3 | m²
Velocity down tip |  | 0.5 | m/s
Height of bag |  | 1.8 | m
Diameter of bag |  | 0.1 | m
Radius of bag |  | 0.31416 | m
Volume down tip |  | 1.5 | m³/s
Surface area of bag |  | 1.268 | m²
Volume through bag |  | 0.1268 | m³/s
12
Number of bags req. |  | 12 Bags
FORMULAE TO CALCULATE THE FLANGE WIDTH PREVENTING AIR DRAWN FROM BEHIND HOOD FACE
Where:
Wt | = | Flange Width (cm)
x | = | distance in front of capture hood along axis (cm)
D | = | duct diameter… round ducts (cm)
Duct Diameter | 57 |  | cm
Capture hood distance "x" | 300 |  | cm
Wt | 15 cm

## DUST Treatment
|  | Product Calculations |  | Revised Nov 2011 |  | Back to INDEX
DusTreat DC9112A - Initial Application |  |  | DusTreat DC9112A - Maintenance
Road Length | 1000 | m | Road Length | 100 | m | Distance (m) | Once / Mth | Twice / Mth | Total
Road Width | 4.8 | m | Road Width | 4.8 | m | 100 | 1988.856 | 1988.856 | 3977.712
Total Surface Area | 4800 | m² | Total Surface Area | 480 | m² | 200 | 3977.712 | 3977.712 | 7955.424
[6 empty] | 300 | 5966.568 | 5966.568 | 11933.136
Solution Spray Rate | 1.6 | L/m² | Solution Spray Rate | 1.5 | L/m² | 400 | 7955.424 | 7955.424 | 15910.848
% Concentration | 0.3 |  | % Concentration of Mix | 0.25 |  | 500 | 9944.28 | 9944.28 | 19888.56
[6 empty] | 600 | 11933.136 | 11933.136 | 23866.272
|  |  | Quantity required to treat "Road Length" | 720 | Litres | 700 | 13921.992 | 13921.992 | 27843.984
Spray Car Size | 3000 | Litres | Spray Car Size | 3000 | Litres | 800 | 15910.848 | 15910.848 | 31821.696
Kg Product per Spray car | 900 | Kg | Kg Product per Spray car | 180 | Liters | 900 | 17899.704 | 17899.704 | 35799.408
Pack size | 23 | Kg | Pack / Drum size | 25 | Liters | 1000 | 19888.56 | 19888.56 | 39777.12
Packs to use | 40 | packs | Number of drums required | 8 | Drums | 1100 | 21877.416 | 21877.416 | 43754.832
|  |  | Cost per 25Liter Drum | 276.23 | Rand | 1200 | 23866.272 | 23866.272 | 47732.544
|  |  | Cost to treat Tunnel | 1988.856 | Rand |  |  | R | 310261.536
25L/Kg = R276.23 May 2013 Price
Revised Nov 2011_CMassyn

## Rectangular gravity settler
Back to INDEX
Rectangular horizontal gravity settler (Using Stokes' law)
Temperature | T | 30 | oC
Local pressure | P | 101 | kPa
Gas density | ρG | 1.1665 | kg/m3 | (Ideal gas law)
Gas viscosity | μG | 1.85e-05 | N.sec/m2 | (Data from Perry as a function of T)
Solids density | ρS | 1590 | kg/m3
Gas flow out of fan | q | 3.1809 | m3/s
Diameter of pipe out of fan | dp | 300 | mm
Cross sectional area of fan outlet | Ap | 0.070686 | m2
Velocity in pipe out of fan | vp | 45 | m/s
Length of settling chamber in direction of gas flow | Ls | 3 | m
Height of settling chamber | Hs | 1 | m
Width of settling chamber | Ws | 0.5 | m
Cross sectional area of settler chamber | As | 0.5 | m2
Gas velocity | Vs | 6.3617 | m/s
Acceleration due to gravity | g | 9.81 | m/s2
Diameter of smallest particle separated out | Dpmin | 0.00021285 | m | Equation 20-57, Perry pp. 20-82
|  | 212.8508 | μm
Particle Reynolds number | NRe | 85.3785
Stokes terminal settling velocity | ut | 2.1206 | m/s | (Stoke's law applies for NRe <0.1)
Hs = 0.3 and Ws = 0.3 |  |  |  | Hs = 0.5 and Ws = 0.5 |  |  | Hs = 1 and Ws = 1
0.3 |  |  |  | 0.5 |  |  | 1
Ls | Dpmin | diff |  | Ls | Dpmin | diff | Ls | Dpmin | diff
1 | 475 |  |  | 1 | 370 |  | 1 | 260
2 | 340 | 135 |  | 2 | 260 | 110 | 2 | 180 | 80
3 | 275 | 65 |  | 3 | 210 | 50 | 3 | 150 | 30
4 | 240 | 35 |  | 4 | 180 | 30 | 4 | 130 | 20
Suggested configuration
+150 um
From fan
To cyclone
-75 um
1000x1000
-150 um
+107 um
-107 um
+87 um
-87 um
+75 um

## Rectangular gravity settler (2)
Back to INDEX
Rectangular horizontal gravity settler (Using drag coefficient calculation)
Temperature |  |  |  |  | T | 25 | oC
Local pressure |  |  |  |  | P | 86 | kPa
Gas density |  |  |  |  | ρG | 1.0099 | kg/m3 | (Ideal gas law)
Gas viscosity |  |  |  |  | μG | 1.825e-05 | N.sec/m2 | (Data from Perry as a function of T)
Solids density |  |  |  |  | ρS | 1590 | kg/m3
Gas flow out of fan |  |  |  |  | q | 2.5 | m3/s
Diameter of pipe out of fan |  |  |  |  | dp | 360 | mm
Cross sectional area of fan outlet |  |  |  |  | Ap | 0.10179 | m2
Velocity in pipe out of fan |  |  |  |  | vp | 24.5609 | m/s
Length of settling chamber in direction of gas flow |  |  |  |  | Ls | 4 | m
Height of settling chamber |  |  |  |  | Hs | 0.4 | m
Width of settling chamber |  |  |  |  | Ws | 0.4 | m
Cross sectional area of settler chamber |  |  |  |  | As | 0.16 | m2
Gas velocity |  |  |  |  | Vs | 15.625 | m/s
Acceleration due to gravity |  |  |  |  | g | 9.81 | m/s2
Particle Reynolds number |  |  |  |  | NRe | 107.5749
Drag coefficient for NRe <1000 but outside Stokes |  |  |  |  | C | 1.0488
Settling velocity for NRe <1000 |  |  |  |  | ut | 1.5625 | m/s
Diameter of smallest particle separated out |  |  |  |  | Dpmin | 0.00012442 | m
[6 empty] | 124.4172 | μm
Hs = 0.4 and Ws = 0.4 |  |  |  | Hs = 0.5 and Ws = 0.5 |  |  |  | Hs = 1 and Ws = 1
0.4 |  |  |  | 0.5 |  |  |  | 1
Ls | Dpmin | diff |  | Ls | Dpmin | diff |  | Ls | Dpmin | diff
1 | 918 |  |  | 1 | 742 |  |  | 1 | 425
2 | 332 | 586 |  | 2 | 274 | 468 |  | 2 | 174 | 251
3 | 186 | 146 |  | 3 | 156 | 118 |  | 3 | 106 | 68
4 | 124 | 62 |  | 4 | 106 | 50 |  | 4 | 75 | 31
Suggested configuration
Efficiency
Ls | Size (um) | 1000 | 800 | 600 | 400 | 200 | 100 | 50 | 25
(m) |  | 0.001 | 0.0008 | 0.0006 | 0.0004 | 0.0002 | 0.0001 | 5e-05 | 2.5e-05
| ut (m/s) | 4.4298 | 3.9621 | 3.4313 | 2.8016 | 1.981 | 1.4008 | 0.99052 | 0.70041
0.5 |  | 0.35438 | 0.31697 | 0.2745 | 0.22413 | 0.15848 | 0.11206 | 0.079242 | 0.056032
1 |  | 0.70876 | 0.63394 | 0.549 | 0.44826 | 0.31697 | 0.22413 | 0.15848 | 0.11206
1.5 |  | 1 | 0.9509 | 0.82351 | 0.67239 | 0.47545 | 0.33619 | 0.23773 | 0.1681
2 |  | 1 | 1 | 1 | 0.89652 | 0.63394 | 0.44826 | 0.31697 | 0.22413
2.5 |  | 1 | 1 | 1 | 1 | 0.79242 | 0.56032 | 0.39621 | 0.28016
3 |  | 1 | 1 | 1 | 1 | 0.9509 | 0.67239 | 0.47545 | 0.33619
3.5 |  | 1 | 1 | 1 | 1 | 1 | 0.78445 | 0.55469 | 0.39223
4 |  | 1 | 1 | 1 | 1 | 1 | 0.89652 | 0.63394 | 0.44826
+918 um
From fan
To cyclone
-124 um
400Hx400W
-918 um
+332 um
-332 um
+186 um
-186 um
+124 um

## Cylindrical gravity settler
Back to INDEX
Cylindrical horizontal gravity settler (Using Stokes' Law)
Temperature | T | 30 | oC
Local pressure | P | 101 | kPa
Gas density | ρG | 1.1665 | kg/m3 | (Ideal gas law)
Gas viscosity | μG | 1.85e-05 | N.sec/m2 | (Data from Perry as a function of T)
Solids density | ρS | 1590 | kg/m3
Gas flow out of fan | G | 3.1809 | m3/s
Diameter of pipe out of fan | dp | 300 | mm
Velocity in pipe out of fan | vp | 45 | m/s
Length of settling chamber in direction of gas flow | Ls | 1 | m
Diameter of settling chamber | Ds | 0.35 | m
Cross sectional area of settler chamber | As | 0.096211 | m2
Gas velocity | Vs | 33.0612 | m/s
Acceleration due to gravity | g | 9.81 | m/s2
Diameter of smallest particle separated out | Dpmin | 0.00049721 | m | Equation 20-57, Perry pp. 20-82
|  | 497.2123 | μm
Ds | 0.35 |  |  | 0.6 |  |  | 1
Ls | Dpmin | diff |  | Ls | Dpmin | diff | Ls | Dpmin | diff
1 | 500 |  |  | 1 | 380 |  | 1 | 300
2 | 350 | 150 |  | 2 | 270 | 110 | 2 | 210 | 90
3 | 290 | 60 |  | 3 | 220 | 50 | 3 | 170 | 40
4 | 250 | 40 |  | 4 | 190 | 30 | 4 | 150 | 20
Suggested configuration
+380 um
From Fan
To cyclone
-190 um
600 Æ
-380 um
+270 um
-270 um
+220 um
-220 um
+190 um

## Stores Req Dev
Ventilation equipment required to ventilate development ends | [7 empty] | Back to INDEX
| Hlge Advance |  |  |  | 100 | m
| RAW Advance |  |  |  | 100 | m
| Conn X/C 1 Length |  |  |  | 30 | m
Conn X/C 2 Due? Y=1 N=0
| Ventilation Collumn Lengths used |  |  |  | 2.24 | m | (Options - 2.24m 4.5m)
| 1015mm / 760mm Column Used |  |  |  | 760 | mm | Bolts per Pipe | 12
| Fans used Primary (kW) |  |  |  | 75 | kW
| Fans used Secondary (kW) |  |  |  | 45 | kW
| Equipment Replacement % |  |  |  | 0.1
[10 empty] | 100 | m
| Conn X/C 1 |  | 30 | m |  |  | Conn X/C 2 |  | 30 | m
[10 empty] | 100 | m
| Equipment |  |  |  | Quantity Total | Unit | Stock Codes |  | Per End | Unit
| 760 | mm Dia. Vent Pipes | 2.24 | m Lengths | 87.4286 | Each |  |  | 43.7143 | Each
| Bends 90° |  |  |  | 5 | Each |  |  | 2.5 | Each
| Bolts M12 |  |  |  | 1155 | Each |  |  | 577.5 | Each
| Bro Spray Waterblast |  |  |  | 2 | Each |  |  | 1 | Each
| Fans used Primary (kW) |  |  |  | 2 | Each |  |  | 1 | Each
| Fans used Secondary (kW) |  |  |  | 1 | Each |  |  | 0.5 | Each
| Suspension Chains 16mm for fans |  |  |  | 15 | m |  |  | 7.5 | m
| Suspension Chains 10mm for Pipes |  |  |  | 875 | m |  |  | 437.5 | m
| Pigtail Eyebolts (5 per fan) |  |  |  | 15 | Each |  |  | 7.5 | Each
| Tubing 1015mm Diameter 50m lengths |  |  |  | 6 | Each |  |  | 3 | Each
Vent Doors
Walls
Stem Pipes
Barricade

## Heat Calc
Back to INDEX
Expected increase in Temp Dev Ends (By M. Symons.)
ENTER
Qty IN | 20 | m³/s
Qty OUT | 1 | m³/s
Length of Collumn | 350 | m
Temp IN | 25.3 | °C
Expected Temp Out : | 26.4827 | °C
AUTO-COMPRESSION OR DE-COMPRESSION
H =
Where
Start depth | 0 | m
End depth | 500 | m
vertical depth | 500 | Z (ΔZ)
g = gravitational acceleration | 9.79 | m/s² | = | 9,79 kJ/kg / 1000m of vertical depth
H = heat increase | 4.895 | °C
VIRGIN ROCK TEMPERATURE [approximate] | [6 empty] | VIRGIN ROCK TEMPERATURE (Calc with Geothermal gradient Data) |  |  |  | Geothermal Gradient (Calc with VRT + depth gradient Data)
| Rock Start Temp °C | Gradient °C/m | 900 | m | = | Depth in m | Geothemal gradient (Eg.: 0.0113) | 0.018 | °C/m | Enter | VRT |  | 46 | °C | Enter
VRT = Gauteng | 16 | 0.0105 | 25.45 | °C |  |  | Geothemal Surface temp | 25.3 | °C | Enter | Geothemal Surface temp |  | 21 | °C | Enter
VRT = Free State | 20 | 0.0146 | 33.14 | °C |  |  | MEAN ROCK BREAKING DEPTH IN METERS | 460 | m | Enter | VRT at DEPTH IN METERS |  | 1200 | m | Enter
VRT = Klerksdorp | 22 | 0.0105 | 31.45 | °C |  |  | VRT = | 33.58 | °C |  | Geothemal gradient (Eg.: 0.0113) |  | 0.020833 | °C/m
VRT = Phalaborwa | 27 | 0.0186 | 43.74 | °C
VRT = Amandelbult / Rtb | 23.9 | 0.0192 | 41.18 | °C
VRT = |  |  | 0 | °C
VRT = |  |  | 0 | °C
VRT = |  |  | 0 | °C
WET KATA FORMULA | [11 empty] | 0.016471
0.020833
H = | [11 empty] | 0.0313
| 33 | Wet Bulb °C
| 0.3 | Velocity m/s
| 3.5 | θ
H = wet kata reading | 4.367 | Millicalories / cm²/sec
Amount of Heat transferred (Conduction)
q =
| 63 | °C | = | Temperature 1
| 37 | °C | = | Temperature 2
| 0.09 | K | = | Thermal conductivity of material [W/m°C]
| 45 | m² | = | Cross-sectional area [m²]
| 0.05 | B | = | Thickness [m]
q = | 2106 | W | = | Conductive heat transfer ratio [W]
For a Tunnel (4 Sides) | 8424 | W
Note on B2: Non Trackless Steel ducting 570mmø

## Vent calculator
Back to INDEX | [31 empty] | Back to INDEX
m² | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 4 | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | m² | 6.3 | 6.8 | 7.3 | 7.6 | 7.8 | 8.1 | 8.7 | 9 | 9.2 | 9.3 | 9.4 | 9.5 | 9.6 | 9.7 | 9.8 | 9.9 | 10.1 | 10.2 | 10.4 | 10.6 | 10.8 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
Vel | [31 empty] | Vel
0.1 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.39 | 0.4 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.1 | 0.63 | 0.68 | 0.73 | 0.76 | 0.78 | 0.81 | 0.87 | 0.9 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 1.01 | 1.02 | 1.04 | 1.06 | 1.08 | 1.1 | 1.15 | 1.2 | 1.25 | 1.3 | 1.35 | 1.4 | 1.45 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.4
0.2 | 0.3 | 0.32 | 0.34 | 0.36 | 0.38 | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | 0.7 | 0.72 | 0.74 | 0.76 | 0.78 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.9 | 0.2 | 1.26 | 1.36 | 1.46 | 1.52 | 1.56 | 1.62 | 1.74 | 1.8 | 1.84 | 1.86 | 1.88 | 1.9 | 1.92 | 1.94 | 1.96 | 1.98 | 2.02 | 2.04 | 2.08 | 2.12 | 2.16 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.2 | 3.4 | 3.6 | 3.8 | 4 | 4.2 | 4.4 | 4.6 | 4.8 | 5 | 5.2 | 5.4 | 5.6 | 5.8 | 6 | 6.2 | 6.4 | 6.6 | 6.8
0.3 | 0.45 | 0.48 | 0.51 | 0.54 | 0.57 | 0.6 | 0.63 | 0.66 | 0.69 | 0.72 | 0.75 | 0.78 | 0.81 | 0.84 | 0.87 | 0.9 | 0.93 | 0.96 | 0.99 | 1.02 | 1.05 | 1.08 | 1.11 | 1.14 | 1.17 | 1.2 | 1.23 | 1.26 | 1.29 | 1.32 | 1.35 | 0.3 | 1.89 | 2.04 | 2.19 | 2.28 | 2.34 | 2.43 | 2.61 | 2.7 | 2.76 | 2.79 | 2.82 | 2.85 | 2.88 | 2.91 | 2.94 | 2.97 | 3.03 | 3.06 | 3.12 | 3.18 | 3.24 | 3.3 | 3.45 | 3.6 | 3.75 | 3.9 | 4.05 | 4.2 | 4.35 | 4.5 | 4.8 | 5.1 | 5.4 | 5.7 | 6 | 6.3 | 6.6 | 6.9 | 7.2 | 7.5 | 7.8 | 8.1 | 8.4 | 8.7 | 9 | 9.3 | 9.6 | 9.9 | 10.2
0.4 | 0.6 | 0.64 | 0.68 | 0.72 | 0.76 | 0.8 | 0.84 | 0.88 | 0.92 | 0.96 | 1 | 1.04 | 1.08 | 1.12 | 1.16 | 1.2 | 1.24 | 1.28 | 1.32 | 1.36 | 1.4 | 1.44 | 1.48 | 1.52 | 1.56 | 1.6 | 1.64 | 1.68 | 1.72 | 1.76 | 1.8 | 0.4 | 2.52 | 2.72 | 2.92 | 3.04 | 3.12 | 3.24 | 3.48 | 3.6 | 3.68 | 3.72 | 3.76 | 3.8 | 3.84 | 3.88 | 3.92 | 3.96 | 4.04 | 4.08 | 4.16 | 4.24 | 4.32 | 4.4 | 4.6 | 4.8 | 5 | 5.2 | 5.4 | 5.6 | 5.8 | 6 | 6.4 | 6.8 | 7.2 | 7.6 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6
0.5 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1 | 1.05 | 1.1 | 1.15 | 1.2 | 1.25 | 1.3 | 1.35 | 1.4 | 1.45 | 1.5 | 1.55 | 1.6 | 1.65 | 1.7 | 1.75 | 1.8 | 1.85 | 1.9 | 1.95 | 2 | 2.05 | 2.1 | 2.15 | 2.2 | 2.25 | 0.5 | 3.15 | 3.4 | 3.65 | 3.8 | 3.9 | 4.05 | 4.35 | 4.5 | 4.6 | 4.65 | 4.7 | 4.75 | 4.8 | 4.85 | 4.9 | 4.95 | 5.05 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.75 | 6 | 6.25 | 6.5 | 6.75 | 7 | 7.25 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17
0.6 | 0.9 | 0.96 | 1.02 | 1.08 | 1.14 | 1.2 | 1.26 | 1.32 | 1.38 | 1.44 | 1.5 | 1.56 | 1.62 | 1.68 | 1.74 | 1.8 | 1.86 | 1.92 | 1.98 | 2.04 | 2.1 | 2.16 | 2.22 | 2.28 | 2.34 | 2.4 | 2.46 | 2.52 | 2.58 | 2.64 | 2.7 | 0.6 | 3.78 | 4.08 | 4.38 | 4.56 | 4.68 | 4.86 | 5.22 | 5.4 | 5.52 | 5.58 | 5.64 | 5.7 | 5.76 | 5.82 | 5.88 | 5.94 | 6.06 | 6.12 | 6.24 | 6.36 | 6.48 | 6.6 | 6.9 | 7.2 | 7.5 | 7.8 | 8.1 | 8.4 | 8.7 | 9 | 9.6 | 10.2 | 10.8 | 11.4 | 12 | 12.6 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 18.6 | 19.2 | 19.8 | 20.4
0.7 | 1.05 | 1.12 | 1.19 | 1.26 | 1.33 | 1.4 | 1.47 | 1.54 | 1.61 | 1.68 | 1.75 | 1.82 | 1.89 | 1.96 | 2.03 | 2.1 | 2.17 | 2.24 | 2.31 | 2.38 | 2.45 | 2.52 | 2.59 | 2.66 | 2.73 | 2.8 | 2.87 | 2.94 | 3.01 | 3.08 | 3.15 | 0.7 | 4.41 | 4.76 | 5.11 | 5.32 | 5.46 | 5.67 | 6.09 | 6.3 | 6.44 | 6.51 | 6.58 | 6.65 | 6.72 | 6.79 | 6.86 | 6.93 | 7.07 | 7.14 | 7.28 | 7.42 | 7.56 | 7.7 | 8.05 | 8.4 | 8.75 | 9.1 | 9.45 | 9.8 | 10.15 | 10.5 | 11.2 | 11.9 | 12.6 | 13.3 | 14 | 14.7 | 15.4 | 16.1 | 16.8 | 17.5 | 18.2 | 18.9 | 19.6 | 20.3 | 21 | 21.7 | 22.4 | 23.1 | 23.8
0.8 | 1.2 | 1.28 | 1.36 | 1.44 | 1.52 | 1.6 | 1.68 | 1.76 | 1.84 | 1.92 | 2 | 2.08 | 2.16 | 2.24 | 2.32 | 2.4 | 2.48 | 2.56 | 2.64 | 2.72 | 2.8 | 2.88 | 2.96 | 3.04 | 3.12 | 3.2 | 3.28 | 3.36 | 3.44 | 3.52 | 3.6 | 0.8 | 5.04 | 5.44 | 5.84 | 6.08 | 6.24 | 6.48 | 6.96 | 7.2 | 7.36 | 7.44 | 7.52 | 7.6 | 7.68 | 7.76 | 7.84 | 7.92 | 8.08 | 8.16 | 8.32 | 8.48 | 8.64 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.8 | 13.6 | 14.4 | 15.2 | 16 | 16.8 | 17.6 | 18.4 | 19.2 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 24.8 | 25.6 | 26.4 | 27.2
0.9 | 1.35 | 1.44 | 1.53 | 1.62 | 1.71 | 1.8 | 1.89 | 1.98 | 2.07 | 2.16 | 2.25 | 2.34 | 2.43 | 2.52 | 2.61 | 2.7 | 2.79 | 2.88 | 2.97 | 3.06 | 3.15 | 3.24 | 3.33 | 3.42 | 3.51 | 3.6 | 3.69 | 3.78 | 3.87 | 3.96 | 4.05 | 0.9 | 5.67 | 6.12 | 6.57 | 6.84 | 7.02 | 7.29 | 7.83 | 8.1 | 8.28 | 8.37 | 8.46 | 8.55 | 8.64 | 8.73 | 8.82 | 8.91 | 9.09 | 9.18 | 9.36 | 9.54 | 9.72 | 9.9 | 10.35 | 10.8 | 11.25 | 11.7 | 12.15 | 12.6 | 13.05 | 13.5 | 14.4 | 15.3 | 16.2 | 17.1 | 18 | 18.9 | 19.8 | 20.7 | 21.6 | 22.5 | 23.4 | 24.3 | 25.2 | 26.1 | 27 | 27.9 | 28.8 | 29.7 | 30.6
1 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 4 | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | 1 | 6.3 | 6.8 | 7.3 | 7.6 | 7.8 | 8.1 | 8.7 | 9 | 9.2 | 9.3 | 9.4 | 9.5 | 9.6 | 9.7 | 9.8 | 9.9 | 10.1 | 10.2 | 10.4 | 10.6 | 10.8 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
1.1 | 1.65 | 1.76 | 1.87 | 1.98 | 2.09 | 2.2 | 2.31 | 2.42 | 2.53 | 2.64 | 2.75 | 2.86 | 2.97 | 3.08 | 3.19 | 3.3 | 3.41 | 3.52 | 3.63 | 3.74 | 3.85 | 3.96 | 4.07 | 4.18 | 4.29 | 4.4 | 4.51 | 4.62 | 4.73 | 4.84 | 4.95 | 1.1 | 6.93 | 7.48 | 8.03 | 8.36 | 8.58 | 8.91 | 9.57 | 9.9 | 10.12 | 10.23 | 10.34 | 10.45 | 10.56 | 10.67 | 10.78 | 10.89 | 11.11 | 11.22 | 11.44 | 11.66 | 11.88 | 12.1 | 12.65 | 13.2 | 13.75 | 14.3 | 14.85 | 15.4 | 15.95 | 16.5 | 17.6 | 18.7 | 19.8 | 20.9 | 22 | 23.1 | 24.2 | 25.3 | 26.4 | 27.5 | 28.6 | 29.7 | 30.8 | 31.9 | 33 | 34.1 | 35.2 | 36.3 | 37.4
1.2 | 1.8 | 1.92 | 2.04 | 2.16 | 2.28 | 2.4 | 2.52 | 2.64 | 2.76 | 2.88 | 3 | 3.12 | 3.24 | 3.36 | 3.48 | 3.6 | 3.72 | 3.84 | 3.96 | 4.08 | 4.2 | 4.32 | 4.44 | 4.56 | 4.68 | 4.8 | 4.92 | 5.04 | 5.16 | 5.28 | 5.4 | 1.2 | 7.56 | 8.16 | 8.76 | 9.12 | 9.36 | 9.72 | 10.44 | 10.8 | 11.04 | 11.16 | 11.28 | 11.4 | 11.52 | 11.64 | 11.76 | 11.88 | 12.12 | 12.24 | 12.48 | 12.72 | 12.96 | 13.2 | 13.8 | 14.4 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 18 | 19.2 | 20.4 | 21.6 | 22.8 | 24 | 25.2 | 26.4 | 27.6 | 28.8 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 37.2 | 38.4 | 39.6 | 40.8
1.3 | 1.95 | 2.08 | 2.21 | 2.34 | 2.47 | 2.6 | 2.73 | 2.86 | 2.99 | 3.12 | 3.25 | 3.38 | 3.51 | 3.64 | 3.77 | 3.9 | 4.03 | 4.16 | 4.29 | 4.42 | 4.55 | 4.68 | 4.81 | 4.94 | 5.07 | 5.2 | 5.33 | 5.46 | 5.59 | 5.72 | 5.85 | 1.3 | 8.19 | 8.84 | 9.49 | 9.88 | 10.14 | 10.53 | 11.31 | 11.7 | 11.96 | 12.09 | 12.22 | 12.35 | 12.48 | 12.61 | 12.74 | 12.87 | 13.13 | 13.26 | 13.52 | 13.78 | 14.04 | 14.3 | 14.95 | 15.6 | 16.25 | 16.9 | 17.55 | 18.2 | 18.85 | 19.5 | 20.8 | 22.1 | 23.4 | 24.7 | 26 | 27.3 | 28.6 | 29.9 | 31.2 | 32.5 | 33.8 | 35.1 | 36.4 | 37.7 | 39 | 40.3 | 41.6 | 42.9 | 44.2
1.4 | 2.1 | 2.24 | 2.38 | 2.52 | 2.66 | 2.8 | 2.94 | 3.08 | 3.22 | 3.36 | 3.5 | 3.64 | 3.78 | 3.92 | 4.06 | 4.2 | 4.34 | 4.48 | 4.62 | 4.76 | 4.9 | 5.04 | 5.18 | 5.32 | 5.46 | 5.6 | 5.74 | 5.88 | 6.02 | 6.16 | 6.3 | 1.4 | 8.82 | 9.52 | 10.22 | 10.64 | 10.92 | 11.34 | 12.18 | 12.6 | 12.88 | 13.02 | 13.16 | 13.3 | 13.44 | 13.58 | 13.72 | 13.86 | 14.14 | 14.28 | 14.56 | 14.84 | 15.12 | 15.4 | 16.1 | 16.8 | 17.5 | 18.2 | 18.9 | 19.6 | 20.3 | 21 | 22.4 | 23.8 | 25.2 | 26.6 | 28 | 29.4 | 30.8 | 32.2 | 33.6 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 43.4 | 44.8 | 46.2 | 47.6
1.5 | 2.25 | 2.4 | 2.55 | 2.7 | 2.85 | 3 | 3.15 | 3.3 | 3.45 | 3.6 | 3.75 | 3.9 | 4.05 | 4.2 | 4.35 | 4.5 | 4.65 | 4.8 | 4.95 | 5.1 | 5.25 | 5.4 | 5.55 | 5.7 | 5.85 | 6 | 6.15 | 6.3 | 6.45 | 6.6 | 6.75 | 1.5 | 9.45 | 10.2 | 10.95 | 11.4 | 11.7 | 12.15 | 13.05 | 13.5 | 13.8 | 13.95 | 14.1 | 14.25 | 14.4 | 14.55 | 14.7 | 14.85 | 15.15 | 15.3 | 15.6 | 15.9 | 16.2 | 16.5 | 17.25 | 18 | 18.75 | 19.5 | 20.25 | 21 | 21.75 | 22.5 | 24 | 25.5 | 27 | 28.5 | 30 | 31.5 | 33 | 34.5 | 36 | 37.5 | 39 | 40.5 | 42 | 43.5 | 45 | 46.5 | 48 | 49.5 | 51
1.6 | 2.4 | 2.56 | 2.72 | 2.88 | 3.04 | 3.2 | 3.36 | 3.52 | 3.68 | 3.84 | 4 | 4.16 | 4.32 | 4.48 | 4.64 | 4.8 | 4.96 | 5.12 | 5.28 | 5.44 | 5.6 | 5.76 | 5.92 | 6.08 | 6.24 | 6.4 | 6.56 | 6.72 | 6.88 | 7.04 | 7.2 | 1.6 | 10.08 | 10.88 | 11.68 | 12.16 | 12.48 | 12.96 | 13.92 | 14.4 | 14.72 | 14.88 | 15.04 | 15.2 | 15.36 | 15.52 | 15.68 | 15.84 | 16.16 | 16.32 | 16.64 | 16.96 | 17.28 | 17.6 | 18.4 | 19.2 | 20 | 20.8 | 21.6 | 22.4 | 23.2 | 24 | 25.6 | 27.2 | 28.8 | 30.4 | 32 | 33.6 | 35.2 | 36.8 | 38.4 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 49.6 | 51.2 | 52.8 | 54.4
1.7 | 2.55 | 2.72 | 2.89 | 3.06 | 3.23 | 3.4 | 3.57 | 3.74 | 3.91 | 4.08 | 4.25 | 4.42 | 4.59 | 4.76 | 4.93 | 5.1 | 5.27 | 5.44 | 5.61 | 5.78 | 5.95 | 6.12 | 6.29 | 6.46 | 6.63 | 6.8 | 6.97 | 7.14 | 7.31 | 7.48 | 7.65 | 1.7 | 10.71 | 11.56 | 12.41 | 12.92 | 13.26 | 13.77 | 14.79 | 15.3 | 15.64 | 15.81 | 15.98 | 16.15 | 16.32 | 16.49 | 16.66 | 16.83 | 17.17 | 17.34 | 17.68 | 18.02 | 18.36 | 18.7 | 19.55 | 20.4 | 21.25 | 22.1 | 22.95 | 23.8 | 24.65 | 25.5 | 27.2 | 28.9 | 30.6 | 32.3 | 34 | 35.7 | 37.4 | 39.1 | 40.8 | 42.5 | 44.2 | 45.9 | 47.6 | 49.3 | 51 | 52.7 | 54.4 | 56.1 | 57.8
1.8 | 2.7 | 2.88 | 3.06 | 3.24 | 3.42 | 3.6 | 3.78 | 3.96 | 4.14 | 4.32 | 4.5 | 4.68 | 4.86 | 5.04 | 5.22 | 5.4 | 5.58 | 5.76 | 5.94 | 6.12 | 6.3 | 6.48 | 6.66 | 6.84 | 7.02 | 7.2 | 7.38 | 7.56 | 7.74 | 7.92 | 8.1 | 1.8 | 11.34 | 12.24 | 13.14 | 13.68 | 14.04 | 14.58 | 15.66 | 16.2 | 16.56 | 16.74 | 16.92 | 17.1 | 17.28 | 17.46 | 17.64 | 17.82 | 18.18 | 18.36 | 18.72 | 19.08 | 19.44 | 19.8 | 20.7 | 21.6 | 22.5 | 23.4 | 24.3 | 25.2 | 26.1 | 27 | 28.8 | 30.6 | 32.4 | 34.2 | 36 | 37.8 | 39.6 | 41.4 | 43.2 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 55.8 | 57.6 | 59.4 | 61.2
1.9 | 2.85 | 3.04 | 3.23 | 3.42 | 3.61 | 3.8 | 3.99 | 4.18 | 4.37 | 4.56 | 4.75 | 4.94 | 5.13 | 5.32 | 5.51 | 5.7 | 5.89 | 6.08 | 6.27 | 6.46 | 6.65 | 6.84 | 7.03 | 7.22 | 7.41 | 7.6 | 7.79 | 7.98 | 8.17 | 8.36 | 8.55 | 1.9 | 11.97 | 12.92 | 13.87 | 14.44 | 14.82 | 15.39 | 16.53 | 17.1 | 17.48 | 17.67 | 17.86 | 18.05 | 18.24 | 18.43 | 18.62 | 18.81 | 19.19 | 19.38 | 19.76 | 20.14 | 20.52 | 20.9 | 21.85 | 22.8 | 23.75 | 24.7 | 25.65 | 26.6 | 27.55 | 28.5 | 30.4 | 32.3 | 34.2 | 36.1 | 38 | 39.9 | 41.8 | 43.7 | 45.6 | 47.5 | 49.4 | 51.3 | 53.2 | 55.1 | 57 | 58.9 | 60.8 | 62.7 | 64.6
2 | 3 | 3.2 | 3.4 | 3.6 | 3.8 | 4 | 4.2 | 4.4 | 4.6 | 4.8 | 5 | 5.2 | 5.4 | 5.6 | 5.8 | 6 | 6.2 | 6.4 | 6.6 | 6.8 | 7 | 7.2 | 7.4 | 7.6 | 7.8 | 8 | 8.2 | 8.4 | 8.6 | 8.8 | 9 | 2 | 12.6 | 13.6 | 14.6 | 15.2 | 15.6 | 16.2 | 17.4 | 18 | 18.4 | 18.6 | 18.8 | 19 | 19.2 | 19.4 | 19.6 | 19.8 | 20.2 | 20.4 | 20.8 | 21.2 | 21.6 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | 60 | 62 | 64 | 66 | 68
2.1 | 3.15 | 3.36 | 3.57 | 3.78 | 3.99 | 4.2 | 4.41 | 4.62 | 4.83 | 5.04 | 5.25 | 5.46 | 5.67 | 5.88 | 6.09 | 6.3 | 6.51 | 6.72 | 6.93 | 7.14 | 7.35 | 7.56 | 7.77 | 7.98 | 8.19 | 8.4 | 8.61 | 8.82 | 9.03 | 9.24 | 9.45 | 2.1 | 13.23 | 14.28 | 15.33 | 15.96 | 16.38 | 17.01 | 18.27 | 18.9 | 19.32 | 19.53 | 19.74 | 19.95 | 20.16 | 20.37 | 20.58 | 20.79 | 21.21 | 21.42 | 21.84 | 22.26 | 22.68 | 23.1 | 24.15 | 25.2 | 26.25 | 27.3 | 28.35 | 29.4 | 30.45 | 31.5 | 33.6 | 35.7 | 37.8 | 39.9 | 42 | 44.1 | 46.2 | 48.3 | 50.4 | 52.5 | 54.6 | 56.7 | 58.8 | 60.9 | 63 | 65.1 | 67.2 | 69.3 | 71.4
2.2 | 3.3 | 3.52 | 3.74 | 3.96 | 4.18 | 4.4 | 4.62 | 4.84 | 5.06 | 5.28 | 5.5 | 5.72 | 5.94 | 6.16 | 6.38 | 6.6 | 6.82 | 7.04 | 7.26 | 7.48 | 7.7 | 7.92 | 8.14 | 8.36 | 8.58 | 8.8 | 9.02 | 9.24 | 9.46 | 9.68 | 9.9 | 2.2 | 13.86 | 14.96 | 16.06 | 16.72 | 17.16 | 17.82 | 19.14 | 19.8 | 20.24 | 20.46 | 20.68 | 20.9 | 21.12 | 21.34 | 21.56 | 21.78 | 22.22 | 22.44 | 22.88 | 23.32 | 23.76 | 24.2 | 25.3 | 26.4 | 27.5 | 28.6 | 29.7 | 30.8 | 31.9 | 33 | 35.2 | 37.4 | 39.6 | 41.8 | 44 | 46.2 | 48.4 | 50.6 | 52.8 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 68.2 | 70.4 | 72.6 | 74.8
2.3 | 3.45 | 3.68 | 3.91 | 4.14 | 4.37 | 4.6 | 4.83 | 5.06 | 5.29 | 5.52 | 5.75 | 5.98 | 6.21 | 6.44 | 6.67 | 6.9 | 7.13 | 7.36 | 7.59 | 7.82 | 8.05 | 8.28 | 8.51 | 8.74 | 8.97 | 9.2 | 9.43 | 9.66 | 9.89 | 10.12 | 10.35 | 2.3 | 14.49 | 15.64 | 16.79 | 17.48 | 17.94 | 18.63 | 20.01 | 20.7 | 21.16 | 21.39 | 21.62 | 21.85 | 22.08 | 22.31 | 22.54 | 22.77 | 23.23 | 23.46 | 23.92 | 24.38 | 24.84 | 25.3 | 26.45 | 27.6 | 28.75 | 29.9 | 31.05 | 32.2 | 33.35 | 34.5 | 36.8 | 39.1 | 41.4 | 43.7 | 46 | 48.3 | 50.6 | 52.9 | 55.2 | 57.5 | 59.8 | 62.1 | 64.4 | 66.7 | 69 | 71.3 | 73.6 | 75.9 | 78.2
2.4 | 3.6 | 3.84 | 4.08 | 4.32 | 4.56 | 4.8 | 5.04 | 5.28 | 5.52 | 5.76 | 6 | 6.24 | 6.48 | 6.72 | 6.96 | 7.2 | 7.44 | 7.68 | 7.92 | 8.16 | 8.4 | 8.64 | 8.88 | 9.12 | 9.36 | 9.6 | 9.84 | 10.08 | 10.32 | 10.56 | 10.8 | 2.4 | 15.12 | 16.32 | 17.52 | 18.24 | 18.72 | 19.44 | 20.88 | 21.6 | 22.08 | 22.32 | 22.56 | 22.8 | 23.04 | 23.28 | 23.52 | 23.76 | 24.24 | 24.48 | 24.96 | 25.44 | 25.92 | 26.4 | 27.6 | 28.8 | 30 | 31.2 | 32.4 | 33.6 | 34.8 | 36 | 38.4 | 40.8 | 43.2 | 45.6 | 48 | 50.4 | 52.8 | 55.2 | 57.6 | 60 | 62.4 | 64.8 | 67.2 | 69.6 | 72 | 74.4 | 76.8 | 79.2 | 81.6
2.5 | 3.75 | 4 | 4.25 | 4.5 | 4.75 | 5 | 5.25 | 5.5 | 5.75 | 6 | 6.25 | 6.5 | 6.75 | 7 | 7.25 | 7.5 | 7.75 | 8 | 8.25 | 8.5 | 8.75 | 9 | 9.25 | 9.5 | 9.75 | 10 | 10.25 | 10.5 | 10.75 | 11 | 11.25 | 2.5 | 15.75 | 17 | 18.25 | 19 | 19.5 | 20.25 | 21.75 | 22.5 | 23 | 23.25 | 23.5 | 23.75 | 24 | 24.25 | 24.5 | 24.75 | 25.25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28.75 | 30 | 31.25 | 32.5 | 33.75 | 35 | 36.25 | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55 | 57.5 | 60 | 62.5 | 65 | 67.5 | 70 | 72.5 | 75 | 77.5 | 80 | 82.5 | 85
2.6 | 3.9 | 4.16 | 4.42 | 4.68 | 4.94 | 5.2 | 5.46 | 5.72 | 5.98 | 6.24 | 6.5 | 6.76 | 7.02 | 7.28 | 7.54 | 7.8 | 8.06 | 8.32 | 8.58 | 8.84 | 9.1 | 9.36 | 9.62 | 9.88 | 10.14 | 10.4 | 10.66 | 10.92 | 11.18 | 11.44 | 11.7 | 2.6 | 16.38 | 17.68 | 18.98 | 19.76 | 20.28 | 21.06 | 22.62 | 23.4 | 23.92 | 24.18 | 24.44 | 24.7 | 24.96 | 25.22 | 25.48 | 25.74 | 26.26 | 26.52 | 27.04 | 27.56 | 28.08 | 28.6 | 29.9 | 31.2 | 32.5 | 33.8 | 35.1 | 36.4 | 37.7 | 39 | 41.6 | 44.2 | 46.8 | 49.4 | 52 | 54.6 | 57.2 | 59.8 | 62.4 | 65 | 67.6 | 70.2 | 72.8 | 75.4 | 78 | 80.6 | 83.2 | 85.8 | 88.4
2.7 | 4.05 | 4.32 | 4.59 | 4.86 | 5.13 | 5.4 | 5.67 | 5.94 | 6.21 | 6.48 | 6.75 | 7.02 | 7.29 | 7.56 | 7.83 | 8.1 | 8.37 | 8.64 | 8.91 | 9.18 | 9.45 | 9.72 | 9.99 | 10.26 | 10.53 | 10.8 | 11.07 | 11.34 | 11.61 | 11.88 | 12.15 | 2.7 | 17.01 | 18.36 | 19.71 | 20.52 | 21.06 | 21.87 | 23.49 | 24.3 | 24.84 | 25.11 | 25.38 | 25.65 | 25.92 | 26.19 | 26.46 | 26.73 | 27.27 | 27.54 | 28.08 | 28.62 | 29.16 | 29.7 | 31.05 | 32.4 | 33.75 | 35.1 | 36.45 | 37.8 | 39.15 | 40.5 | 43.2 | 45.9 | 48.6 | 51.3 | 54 | 56.7 | 59.4 | 62.1 | 64.8 | 67.5 | 70.2 | 72.9 | 75.6 | 78.3 | 81 | 83.7 | 86.4 | 89.1 | 91.8
2.8 | 4.2 | 4.48 | 4.76 | 5.04 | 5.32 | 5.6 | 5.88 | 6.16 | 6.44 | 6.72 | 7 | 7.28 | 7.56 | 7.84 | 8.12 | 8.4 | 8.68 | 8.96 | 9.24 | 9.52 | 9.8 | 10.08 | 10.36 | 10.64 | 10.92 | 11.2 | 11.48 | 11.76 | 12.04 | 12.32 | 12.6 | 2.8 | 17.64 | 19.04 | 20.44 | 21.28 | 21.84 | 22.68 | 24.36 | 25.2 | 25.76 | 26.04 | 26.32 | 26.6 | 26.88 | 27.16 | 27.44 | 27.72 | 28.28 | 28.56 | 29.12 | 29.68 | 30.24 | 30.8 | 32.2 | 33.6 | 35 | 36.4 | 37.8 | 39.2 | 40.6 | 42 | 44.8 | 47.6 | 50.4 | 53.2 | 56 | 58.8 | 61.6 | 64.4 | 67.2 | 70 | 72.8 | 75.6 | 78.4 | 81.2 | 84 | 86.8 | 89.6 | 92.4 | 95.2
2.9 | 4.35 | 4.64 | 4.93 | 5.22 | 5.51 | 5.8 | 6.09 | 6.38 | 6.67 | 6.96 | 7.25 | 7.54 | 7.83 | 8.12 | 8.41 | 8.7 | 8.99 | 9.28 | 9.57 | 9.86 | 10.15 | 10.44 | 10.73 | 11.02 | 11.31 | 11.6 | 11.89 | 12.18 | 12.47 | 12.76 | 13.05 | 2.9 | 18.27 | 19.72 | 21.17 | 22.04 | 22.62 | 23.49 | 25.23 | 26.1 | 26.68 | 26.97 | 27.26 | 27.55 | 27.84 | 28.13 | 28.42 | 28.71 | 29.29 | 29.58 | 30.16 | 30.74 | 31.32 | 31.9 | 33.35 | 34.8 | 36.25 | 37.7 | 39.15 | 40.6 | 42.05 | 43.5 | 46.4 | 49.3 | 52.2 | 55.1 | 58 | 60.9 | 63.8 | 66.7 | 69.6 | 72.5 | 75.4 | 78.3 | 81.2 | 84.1 | 87 | 89.9 | 92.8 | 95.7 | 98.6
3 | 4.5 | 4.8 | 5.1 | 5.4 | 5.7 | 6 | 6.3 | 6.6 | 6.9 | 7.2 | 7.5 | 7.8 | 8.1 | 8.4 | 8.7 | 9 | 9.3 | 9.6 | 9.9 | 10.2 | 10.5 | 10.8 | 11.1 | 11.4 | 11.7 | 12 | 12.3 | 12.6 | 12.9 | 13.2 | 13.5 | 3 | 18.9 | 20.4 | 21.9 | 22.8 | 23.4 | 24.3 | 26.1 | 27 | 27.6 | 27.9 | 28.2 | 28.5 | 28.8 | 29.1 | 29.4 | 29.7 | 30.3 | 30.6 | 31.2 | 31.8 | 32.4 | 33 | 34.5 | 36 | 37.5 | 39 | 40.5 | 42 | 43.5 | 45 | 48 | 51 | 54 | 57 | 60 | 63 | 66 | 69 | 72 | 75 | 78 | 81 | 84 | 87 | 90 | 93 | 96 | 99 | 102
3.1 | 4.65 | 4.96 | 5.27 | 5.58 | 5.89 | 6.2 | 6.51 | 6.82 | 7.13 | 7.44 | 7.75 | 8.06 | 8.37 | 8.68 | 8.99 | 9.3 | 9.61 | 9.92 | 10.23 | 10.54 | 10.85 | 11.16 | 11.47 | 11.78 | 12.09 | 12.4 | 12.71 | 13.02 | 13.33 | 13.64 | 13.95 | 3.1 | 19.53 | 21.08 | 22.63 | 23.56 | 24.18 | 25.11 | 26.97 | 27.9 | 28.52 | 28.83 | 29.14 | 29.45 | 29.76 | 30.07 | 30.38 | 30.69 | 31.31 | 31.62 | 32.24 | 32.86 | 33.48 | 34.1 | 35.65 | 37.2 | 38.75 | 40.3 | 41.85 | 43.4 | 44.95 | 46.5 | 49.6 | 52.7 | 55.8 | 58.9 | 62 | 65.1 | 68.2 | 71.3 | 74.4 | 77.5 | 80.6 | 83.7 | 86.8 | 89.9 | 93 | 96.1 | 99.2 | 102.3 | 105.4
3.2 | 4.8 | 5.12 | 5.44 | 5.76 | 6.08 | 6.4 | 6.72 | 7.04 | 7.36 | 7.68 | 8 | 8.32 | 8.64 | 8.96 | 9.28 | 9.6 | 9.92 | 10.24 | 10.56 | 10.88 | 11.2 | 11.52 | 11.84 | 12.16 | 12.48 | 12.8 | 13.12 | 13.44 | 13.76 | 14.08 | 14.4 | 3.2 | 20.16 | 21.76 | 23.36 | 24.32 | 24.96 | 25.92 | 27.84 | 28.8 | 29.44 | 29.76 | 30.08 | 30.4 | 30.72 | 31.04 | 31.36 | 31.68 | 32.32 | 32.64 | 33.28 | 33.92 | 34.56 | 35.2 | 36.8 | 38.4 | 40 | 41.6 | 43.2 | 44.8 | 46.4 | 48 | 51.2 | 54.4 | 57.6 | 60.8 | 64 | 67.2 | 70.4 | 73.6 | 76.8 | 80 | 83.2 | 86.4 | 89.6 | 92.8 | 96 | 99.2 | 102.4 | 105.6 | 108.8
3.3 | 4.95 | 5.28 | 5.61 | 5.94 | 6.27 | 6.6 | 6.93 | 7.26 | 7.59 | 7.92 | 8.25 | 8.58 | 8.91 | 9.24 | 9.57 | 9.9 | 10.23 | 10.56 | 10.89 | 11.22 | 11.55 | 11.88 | 12.21 | 12.54 | 12.87 | 13.2 | 13.53 | 13.86 | 14.19 | 14.52 | 14.85 | 3.3 | 20.79 | 22.44 | 24.09 | 25.08 | 25.74 | 26.73 | 28.71 | 29.7 | 30.36 | 30.69 | 31.02 | 31.35 | 31.68 | 32.01 | 32.34 | 32.67 | 33.33 | 33.66 | 34.32 | 34.98 | 35.64 | 36.3 | 37.95 | 39.6 | 41.25 | 42.9 | 44.55 | 46.2 | 47.85 | 49.5 | 52.8 | 56.1 | 59.4 | 62.7 | 66 | 69.3 | 72.6 | 75.9 | 79.2 | 82.5 | 85.8 | 89.1 | 92.4 | 95.7 | 99 | 102.3 | 105.6 | 108.9 | 112.2
3.4 | 5.1 | 5.44 | 5.78 | 6.12 | 6.46 | 6.8 | 7.14 | 7.48 | 7.82 | 8.16 | 8.5 | 8.84 | 9.18 | 9.52 | 9.86 | 10.2 | 10.54 | 10.88 | 11.22 | 11.56 | 11.9 | 12.24 | 12.58 | 12.92 | 13.26 | 13.6 | 13.94 | 14.28 | 14.62 | 14.96 | 15.3 | 3.4 | 21.42 | 23.12 | 24.82 | 25.84 | 26.52 | 27.54 | 29.58 | 30.6 | 31.28 | 31.62 | 31.96 | 32.3 | 32.64 | 32.98 | 33.32 | 33.66 | 34.34 | 34.68 | 35.36 | 36.04 | 36.72 | 37.4 | 39.1 | 40.8 | 42.5 | 44.2 | 45.9 | 47.6 | 49.3 | 51 | 54.4 | 57.8 | 61.2 | 64.6 | 68 | 71.4 | 74.8 | 78.2 | 81.6 | 85 | 88.4 | 91.8 | 95.2 | 98.6 | 102 | 105.4 | 108.8 | 112.2 | 115.6
3.5 | 5.25 | 5.6 | 5.95 | 6.3 | 6.65 | 7 | 7.35 | 7.7 | 8.05 | 8.4 | 8.75 | 9.1 | 9.45 | 9.8 | 10.15 | 10.5 | 10.85 | 11.2 | 11.55 | 11.9 | 12.25 | 12.6 | 12.95 | 13.3 | 13.65 | 14 | 14.35 | 14.7 | 15.05 | 15.4 | 15.75 | 3.5 | 22.05 | 23.8 | 25.55 | 26.6 | 27.3 | 28.35 | 30.45 | 31.5 | 32.2 | 32.55 | 32.9 | 33.25 | 33.6 | 33.95 | 34.3 | 34.65 | 35.35 | 35.7 | 36.4 | 37.1 | 37.8 | 38.5 | 40.25 | 42 | 43.75 | 45.5 | 47.25 | 49 | 50.75 | 52.5 | 56 | 59.5 | 63 | 66.5 | 70 | 73.5 | 77 | 80.5 | 84 | 87.5 | 91 | 94.5 | 98 | 101.5 | 105 | 108.5 | 112 | 115.5 | 119
3.6 | 5.4 | 5.76 | 6.12 | 6.48 | 6.84 | 7.2 | 7.56 | 7.92 | 8.28 | 8.64 | 9 | 9.36 | 9.72 | 10.08 | 10.44 | 10.8 | 11.16 | 11.52 | 11.88 | 12.24 | 12.6 | 12.96 | 13.32 | 13.68 | 14.04 | 14.4 | 14.76 | 15.12 | 15.48 | 15.84 | 16.2 | 3.6 | 22.68 | 24.48 | 26.28 | 27.36 | 28.08 | 29.16 | 31.32 | 32.4 | 33.12 | 33.48 | 33.84 | 34.2 | 34.56 | 34.92 | 35.28 | 35.64 | 36.36 | 36.72 | 37.44 | 38.16 | 38.88 | 39.6 | 41.4 | 43.2 | 45 | 46.8 | 48.6 | 50.4 | 52.2 | 54 | 57.6 | 61.2 | 64.8 | 68.4 | 72 | 75.6 | 79.2 | 82.8 | 86.4 | 90 | 93.6 | 97.2 | 100.8 | 104.4 | 108 | 111.6 | 115.2 | 118.8 | 122.4
3.7 | 5.55 | 5.92 | 6.29 | 6.66 | 7.03 | 7.4 | 7.77 | 8.14 | 8.51 | 8.88 | 9.25 | 9.62 | 9.99 | 10.36 | 10.73 | 11.1 | 11.47 | 11.84 | 12.21 | 12.58 | 12.95 | 13.32 | 13.69 | 14.06 | 14.43 | 14.8 | 15.17 | 15.54 | 15.91 | 16.28 | 16.65 | 3.7 | 23.31 | 25.16 | 27.01 | 28.12 | 28.86 | 29.97 | 32.19 | 33.3 | 34.04 | 34.41 | 34.78 | 35.15 | 35.52 | 35.89 | 36.26 | 36.63 | 37.37 | 37.74 | 38.48 | 39.22 | 39.96 | 40.7 | 42.55 | 44.4 | 46.25 | 48.1 | 49.95 | 51.8 | 53.65 | 55.5 | 59.2 | 62.9 | 66.6 | 70.3 | 74 | 77.7 | 81.4 | 85.1 | 88.8 | 92.5 | 96.2 | 99.9 | 103.6 | 107.3 | 111 | 114.7 | 118.4 | 122.1 | 125.8
3.8 | 5.7 | 6.08 | 6.46 | 6.84 | 7.22 | 7.6 | 7.98 | 8.36 | 8.74 | 9.12 | 9.5 | 9.88 | 10.26 | 10.64 | 11.02 | 11.4 | 11.78 | 12.16 | 12.54 | 12.92 | 13.3 | 13.68 | 14.06 | 14.44 | 14.82 | 15.2 | 15.58 | 15.96 | 16.34 | 16.72 | 17.1 | 3.8 | 23.94 | 25.84 | 27.74 | 28.88 | 29.64 | 30.78 | 33.06 | 34.2 | 34.96 | 35.34 | 35.72 | 36.1 | 36.48 | 36.86 | 37.24 | 37.62 | 38.38 | 38.76 | 39.52 | 40.28 | 41.04 | 41.8 | 43.7 | 45.6 | 47.5 | 49.4 | 51.3 | 53.2 | 55.1 | 57 | 60.8 | 64.6 | 68.4 | 72.2 | 76 | 79.8 | 83.6 | 87.4 | 91.2 | 95 | 98.8 | 102.6 | 106.4 | 110.2 | 114 | 117.8 | 121.6 | 125.4 | 129.2
3.9 | 5.85 | 6.24 | 6.63 | 7.02 | 7.41 | 7.8 | 8.19 | 8.58 | 8.97 | 9.36 | 9.75 | 10.14 | 10.53 | 10.92 | 11.31 | 11.7 | 12.09 | 12.48 | 12.87 | 13.26 | 13.65 | 14.04 | 14.43 | 14.82 | 15.21 | 15.6 | 15.99 | 16.38 | 16.77 | 17.16 | 17.55 | 3.9 | 24.57 | 26.52 | 28.47 | 29.64 | 30.42 | 31.59 | 33.93 | 35.1 | 35.88 | 36.27 | 36.66 | 37.05 | 37.44 | 37.83 | 38.22 | 38.61 | 39.39 | 39.78 | 40.56 | 41.34 | 42.12 | 42.9 | 44.85 | 46.8 | 48.75 | 50.7 | 52.65 | 54.6 | 56.55 | 58.5 | 62.4 | 66.3 | 70.2 | 74.1 | 78 | 81.9 | 85.8 | 89.7 | 93.6 | 97.5 | 101.4 | 105.3 | 109.2 | 113.1 | 117 | 120.9 | 124.8 | 128.7 | 132.6
4 | 6 | 6.4 | 6.8 | 7.2 | 7.6 | 8 | 8.4 | 8.8 | 9.2 | 9.6 | 10 | 10.4 | 10.8 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.2 | 13.6 | 14 | 14.4 | 14.8 | 15.2 | 15.6 | 16 | 16.4 | 16.8 | 17.2 | 17.6 | 18 | 4 | 25.2 | 27.2 | 29.2 | 30.4 | 31.2 | 32.4 | 34.8 | 36 | 36.8 | 37.2 | 37.6 | 38 | 38.4 | 38.8 | 39.2 | 39.6 | 40.4 | 40.8 | 41.6 | 42.4 | 43.2 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | 60 | 64 | 68 | 72 | 76 | 80 | 84 | 88 | 92 | 96 | 100 | 104 | 108 | 112 | 116 | 120 | 124 | 128 | 132 | 136
4.1 | 6.15 | 6.56 | 6.97 | 7.38 | 7.79 | 8.2 | 8.61 | 9.02 | 9.43 | 9.84 | 10.25 | 10.66 | 11.07 | 11.48 | 11.89 | 12.3 | 12.71 | 13.12 | 13.53 | 13.94 | 14.35 | 14.76 | 15.17 | 15.58 | 15.99 | 16.4 | 16.81 | 17.22 | 17.63 | 18.04 | 18.45 | 4.1 | 25.83 | 27.88 | 29.93 | 31.16 | 31.98 | 33.21 | 35.67 | 36.9 | 37.72 | 38.13 | 38.54 | 38.95 | 39.36 | 39.77 | 40.18 | 40.59 | 41.41 | 41.82 | 42.64 | 43.46 | 44.28 | 45.1 | 47.15 | 49.2 | 51.25 | 53.3 | 55.35 | 57.4 | 59.45 | 61.5 | 65.6 | 69.7 | 73.8 | 77.9 | 82 | 86.1 | 90.2 | 94.3 | 98.4 | 102.5 | 106.6 | 110.7 | 114.8 | 118.9 | 123 | 127.1 | 131.2 | 135.3 | 139.4
4.2 | 6.3 | 6.72 | 7.14 | 7.56 | 7.98 | 8.4 | 8.82 | 9.24 | 9.66 | 10.08 | 10.5 | 10.92 | 11.34 | 11.76 | 12.18 | 12.6 | 13.02 | 13.44 | 13.86 | 14.28 | 14.7 | 15.12 | 15.54 | 15.96 | 16.38 | 16.8 | 17.22 | 17.64 | 18.06 | 18.48 | 18.9 | 4.2 | 26.46 | 28.56 | 30.66 | 31.92 | 32.76 | 34.02 | 36.54 | 37.8 | 38.64 | 39.06 | 39.48 | 39.9 | 40.32 | 40.74 | 41.16 | 41.58 | 42.42 | 42.84 | 43.68 | 44.52 | 45.36 | 46.2 | 48.3 | 50.4 | 52.5 | 54.6 | 56.7 | 58.8 | 60.9 | 63 | 67.2 | 71.4 | 75.6 | 79.8 | 84 | 88.2 | 92.4 | 96.6 | 100.8 | 105 | 109.2 | 113.4 | 117.6 | 121.8 | 126 | 130.2 | 134.4 | 138.6 | 142.8
4.3 | 6.45 | 6.88 | 7.31 | 7.74 | 8.17 | 8.6 | 9.03 | 9.46 | 9.89 | 10.32 | 10.75 | 11.18 | 11.61 | 12.04 | 12.47 | 12.9 | 13.33 | 13.76 | 14.19 | 14.62 | 15.05 | 15.48 | 15.91 | 16.34 | 16.77 | 17.2 | 17.63 | 18.06 | 18.49 | 18.92 | 19.35 | 4.3 | 27.09 | 29.24 | 31.39 | 32.68 | 33.54 | 34.83 | 37.41 | 38.7 | 39.56 | 39.99 | 40.42 | 40.85 | 41.28 | 41.71 | 42.14 | 42.57 | 43.43 | 43.86 | 44.72 | 45.58 | 46.44 | 47.3 | 49.45 | 51.6 | 53.75 | 55.9 | 58.05 | 60.2 | 62.35 | 64.5 | 68.8 | 73.1 | 77.4 | 81.7 | 86 | 90.3 | 94.6 | 98.9 | 103.2 | 107.5 | 111.8 | 116.1 | 120.4 | 124.7 | 129 | 133.3 | 137.6 | 141.9 | 146.2
4.4 | 6.6 | 7.04 | 7.48 | 7.92 | 8.36 | 8.8 | 9.24 | 9.68 | 10.12 | 10.56 | 11 | 11.44 | 11.88 | 12.32 | 12.76 | 13.2 | 13.64 | 14.08 | 14.52 | 14.96 | 15.4 | 15.84 | 16.28 | 16.72 | 17.16 | 17.6 | 18.04 | 18.48 | 18.92 | 19.36 | 19.8 | 4.4 | 27.72 | 29.92 | 32.12 | 33.44 | 34.32 | 35.64 | 38.28 | 39.6 | 40.48 | 40.92 | 41.36 | 41.8 | 42.24 | 42.68 | 43.12 | 43.56 | 44.44 | 44.88 | 45.76 | 46.64 | 47.52 | 48.4 | 50.6 | 52.8 | 55 | 57.2 | 59.4 | 61.6 | 63.8 | 66 | 70.4 | 74.8 | 79.2 | 83.6 | 88 | 92.4 | 96.8 | 101.2 | 105.6 | 110 | 114.4 | 118.8 | 123.2 | 127.6 | 132 | 136.4 | 140.8 | 145.2 | 149.6
4.5 | 6.75 | 7.2 | 7.65 | 8.1 | 8.55 | 9 | 9.45 | 9.9 | 10.35 | 10.8 | 11.25 | 11.7 | 12.15 | 12.6 | 13.05 | 13.5 | 13.95 | 14.4 | 14.85 | 15.3 | 15.75 | 16.2 | 16.65 | 17.1 | 17.55 | 18 | 18.45 | 18.9 | 19.35 | 19.8 | 20.25 | 4.5 | 28.35 | 30.6 | 32.85 | 34.2 | 35.1 | 36.45 | 39.15 | 40.5 | 41.4 | 41.85 | 42.3 | 42.75 | 43.2 | 43.65 | 44.1 | 44.55 | 45.45 | 45.9 | 46.8 | 47.7 | 48.6 | 49.5 | 51.75 | 54 | 56.25 | 58.5 | 60.75 | 63 | 65.25 | 67.5 | 72 | 76.5 | 81 | 85.5 | 90 | 94.5 | 99 | 103.5 | 108 | 112.5 | 117 | 121.5 | 126 | 130.5 | 135 | 139.5 | 144 | 148.5 | 153
4.6 | 6.9 | 7.36 | 7.82 | 8.28 | 8.74 | 9.2 | 9.66 | 10.12 | 10.58 | 11.04 | 11.5 | 11.96 | 12.42 | 12.88 | 13.34 | 13.8 | 14.26 | 14.72 | 15.18 | 15.64 | 16.1 | 16.56 | 17.02 | 17.48 | 17.94 | 18.4 | 18.86 | 19.32 | 19.78 | 20.24 | 20.7 | 4.6 | 28.98 | 31.28 | 33.58 | 34.96 | 35.88 | 37.26 | 40.02 | 41.4 | 42.32 | 42.78 | 43.24 | 43.7 | 44.16 | 44.62 | 45.08 | 45.54 | 46.46 | 46.92 | 47.84 | 48.76 | 49.68 | 50.6 | 52.9 | 55.2 | 57.5 | 59.8 | 62.1 | 64.4 | 66.7 | 69 | 73.6 | 78.2 | 82.8 | 87.4 | 92 | 96.6 | 101.2 | 105.8 | 110.4 | 115 | 119.6 | 124.2 | 128.8 | 133.4 | 138 | 142.6 | 147.2 | 151.8 | 156.4
4.7 | 7.05 | 7.52 | 7.99 | 8.46 | 8.93 | 9.4 | 9.87 | 10.34 | 10.81 | 11.28 | 11.75 | 12.22 | 12.69 | 13.16 | 13.63 | 14.1 | 14.57 | 15.04 | 15.51 | 15.98 | 16.45 | 16.92 | 17.39 | 17.86 | 18.33 | 18.8 | 19.27 | 19.74 | 20.21 | 20.68 | 21.15 | 4.7 | 29.61 | 31.96 | 34.31 | 35.72 | 36.66 | 38.07 | 40.89 | 42.3 | 43.24 | 43.71 | 44.18 | 44.65 | 45.12 | 45.59 | 46.06 | 46.53 | 47.47 | 47.94 | 48.88 | 49.82 | 50.76 | 51.7 | 54.05 | 56.4 | 58.75 | 61.1 | 63.45 | 65.8 | 68.15 | 70.5 | 75.2 | 79.9 | 84.6 | 89.3 | 94 | 98.7 | 103.4 | 108.1 | 112.8 | 117.5 | 122.2 | 126.9 | 131.6 | 136.3 | 141 | 145.7 | 150.4 | 155.1 | 159.8

## Flammable gas
Use of calculation | [9 empty] | Back to INDEX
Only edit cells coloured | [10 empty] | https://www.mathesongas.com/pdfs/products/Lower-(LEL)-&-Upper-(UEL)-Explosive-Limits-.pdf
By: Leon du Toit
Calculation of explosive ranges from gas analysis
|  | L1 | L2 | L3 | L4 | L5 | L6
|  | CH4 | H2 | C4H10 | C3H8 | H2S | C2H6
|  | Methane | Hydrogen | Butane | Propane | Hydrogen Sulphide | Ethane
| Lower % | 5 | 4 | 1.8 | 2.37 | 4.3 | 3
| Upper % | 15 | 74 | 8.5 | 9.5 | 46 | 12.5
| Ignition temp |  |  | 500 | 540 | 260 | 472
| Sample Volume | P1 | P2 | P3 | P4 | P5 | P6
|  | 13.26 | 4.48 | 0.01 | 0.14 | 0 | 0.69
LEL | 100/(P1/L1+P2/L2+P3/L3+P4/L4) | LEL % | 33.9371
P=% gas in mixture volume
L=Lower explosion limit %
UEL | 100/(P1/U1+P2/2+P3/3+P4/4) | UEL % | 104.6996
P=% gas in mixture volume
U=Lower explosion limit %
Calculation for the egress of gas from an intersection
Hole diameter | Hole diameter | Hole area | Velocity | Volume | Flammable gas content | Volume gas concentrate | Through vent | Total volume | Gas volume in atmosphere
mm | m | m2 | m/s | m3/s | % | m3/s | m3/s | m3/s | %
48 | 0.048 | 0.0018096 | 500 | 0.90478 | 0.1878 | 0.16992 | 12.1 | 13.0048 | 1.3066
Calculation of gas concentrations after dilution
|  | Flammable gas mixture | Oxygen
| Lower % | 33.9371 | 0
| Upper % | 104.6996 | 0
| Volume | 0.16992 | 12.1
New LEL | (LEL*volume)/total volume mixture | LEL % | 0.46997
New UEL | (UEL*volume)/total volume mixture | UEL % | 1.4499
Note on E14: ledutoit: adapt formula to include gases applicable
Note on E17: ledutoit: adapt formula to include gases applicable
Note on B24: ledutoit: insert hole diameter
Note on E24: Du Toit, Leon: assumed to be terminal velocity
Note on G24: Get % from Gas Analysis Sample report
Note on I24: ledutoit: Insert through volume applicable

## Airchange re-entry
Back to INDEX
|  | Re-Entry Calculator | [11 empty] | Re-Entry Calculator | [10 empty] | 21.85
|  | Length of End / Building | 50.6 | m | [9 empty] | Length of Silo / Shaft |  | 1000 | m | [7 empty] | 23.6
|  | Height of End / Building | 2.4 | m | [9 empty] | Diameter of Silo / Shaft |  | 7 | m | [7 empty] | 9.353
|  | Width of End / Building | 2.6 | m | [9 empty] | Area of Silo / Shaft |  | 38.4845 | m²
|  | Volume of End / Building | 315.744 | m³ | [9 empty] | Volume of Silo / Shaft |  | 38484.51 | m³
|  | Airchanges Required. | 22.5 | No/hr | [9 empty] | Airchanges Required. |  | 1 | No/hr
|  | Qty of Available air. | 1.98 | m³/s |  | hours |  | minutes |  | seconds |  |  |  | Qty of Available air. |  | 40 | m³/s
|  | Re Entry | 0.99667 | Hrs | 59 | [8 empty] | Re Entry |  | 0.26725 | Hrs
|  | Thus time for re-entry is : |  |  | 59.8 | Minutes | [7 empty] | Thus time for re-entry is : |  |  | 16.1 | Minutes
|  | Velocity | 0.31731 | m/s | 0 | hr | 59 | min | 48 | sec | [6 empty] | 0 | hr | 16 | min | 2 | sec
[5 empty] | 0 hr 59 min 48 sec | [11 empty] | 0 hr 16 min 2 sec
[5 empty] | 0 hours 59 minutes 48 seconds | [11 empty] | 0 hours 16 minutes 2 seconds
|  | Airchange (Play with Volumes). | [11 empty] | Airchange (Play with Volumes).
|  | Qty at fan | 41 | m³/s | [9 empty] | Qty at fan |  | 25 | m³/s
|  | TOTAL Leakage (Enter as fraction) | 0.219 | Total Leakage (i.e.. 100m @ 10% = 0.1... 200m @ 10% = 0.2) | [9 empty] | TOTAL Leakage |  | 0.25 | Total Leakage (i.e.. 100m @ 10% = 0.1... 200m @ 10% = 0.2)
|  | Qty at face min Entered % leakage per 100m | 32.021 | m³/s | [9 empty] | Qty at face min Entered % leakage per 100m |  | 18.75 | m³/s
Re-Entry Calculator - Long Columns
|  | Minimum Face Velocity m/s/m² | 0.15 | Minimum Volume
|  | Duct Distance to Face (m) | 12 | 1.35 | m³/s
|  | Airchanges Required. | 8 | No/hr
|  | Duct / End 1 Length increments = (in meters) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | Duct / End 1 Length of End / Building (m) | 22 | 32 | 42 | 52 | 62 | 72 | 82 | 92 | 102 | 112 | 122 | 132 | 142 | 152 | 162 | 172 | 182 | 192 | 202 | 212 | 222 | 232 | 242 | 252 | 262 | 272 | 282
|  | Height of End / Building (m) | 22: 3; 32: m; 72: 2.7; 82: 8.7
|  | Width of End / Building (m) | 22: 3; 32: m; 72: 6; 102: #REF!
|  | Incremental Volume of End / Building (m³) | 198 | 288 | 378 | 468 | 558 | 648 | 738 | 828 | 918 | 1008 | 1098 | 1188 | 1278 | 1368 | 1458 | 1548 | 1638 | 1728 | 1818 | 1908 | 1998 | 2088 | 2178 | 2268 | 2358 | 2448 | 2538
|  | End 1 Qty (m³/s) | 12 | 10.8 | 9.72 | 8.748 | 7.8732 | 7.0859 | 6.3773 | 5.7396 | 5.1656 | 4.649 | 4.1841 | 3.7657 | 3.3892 | 3.0502 | 2.7452 | 2.4707 | 2.2236 | 2.0013 | 1.8011 | 1.621 | 1.4589 | 1.313 | 1.1817 | 1.0636 | 0.9572 | 0.86148 | 0.77533
|  | Leakage Allowed / Actual | 22: 10%; 32: /100m; 42: 0.01; 52: /100m; 102: 0.052261; 112: 0.54695
|  | Calculated Re-Entry Section (Hrs) | 0.036667 | 0.059259 | 0.08642 | 0.11888 | 0.1575 | 0.20322 | 0.25716 | 0.32058 | 0.39492 | 0.48182 | 0.58315 | 0.70106 | 0.83797 | 0.99664 | 1.1802 | 1.3923 | 1.637 | 1.9188 | 2.243 | 2.6156 | 3.0433 | 3.5338 | 4.0957 | 4.7388 | 5.4743 | 6.3147 | 7.2743
|  | Calculated Re-Entry over distance (Hrs) | 0.022593 | 0.02716 | 0.032465 | 0.038612 | 0.045725 | 0.053941 | 0.063419 | 0.074338 | 0.0869 | 0.10134 | 0.11791 | 0.13691 | 0.15868 | 0.18359 | 0.21209 | 0.24465 | 0.28182 | 0.32424 | 0.3726 | 0.42771 | 0.49047 | 0.56189 | 0.64313 | 0.73548 | 0.84042 | 0.95959 | -7.2743
|  | Calculated Re-Entry over distance (Minutes) | 1 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12 | 14 | 16 | 19 | 22 | 25 | 29 | 33 | 38 | 44 | 50 | 57 | 43
|  | End 1 Cumulative (Minutes) | 1 | 2 | 3 | 5 | 7 | 10 | 13 | 17 | 22 | 28 | 35 | 43 | 52 | 63 | 75 | 89 | 105 | 124 | 146 | 171 | 200 | 233 | 271 | 315 | 365 | 422 | 465
|  | End 2 (Series End) starts at: | 22: 60; 32: m
|  | Available Volume (Fan 1) | 22: 8.748; 32: m³/s; 42: NOTE if RED Fan 2 will RECIRCULATE
|  | End 2 Overlap Velocity REQUIRED | 22: 0.3; 32: m/s
|  | Duct / End 2 Length of End / Building (m) | 22 | 32 | 42 | 52 | 62 | 72 | 82 | 92 | 102 | 112 | 122 | 132 | 142 | 152 | 162 | 172 | 182
|  | Height of End / Building (m) | 0.3 22: 3; m/s 32: m; m/s 42: Minimum Volume End 2
|  | Width of End / Building (m) | 0.3 22: 3; m/s 32: m; m/s 42: 1.35; m/s 52: m³/s
|  | End 2 OVERLAP Volume REQUIRED | 0.3 22: 2.7; m/s 32: m³/s
|  | End 2 Available Fan Volume | 5.5 | 4.95 | 4.455 | 4.0095 | 3.6086 | 3.2477 | 2.9229 | 2.6306 | 2.3676 | 2.1308 | 1.9177 | 1.726 | 1.5534 | 1.398 | 1.2582 | 1.1324 | 1.0192
|  | Leakage Allowed / Actual | 0.3 22: 10%; m/s 32: /100m
|  | TOTAL Volume Required End 2 | 0.3 22: 8.2; m/s 32: m³/s
|  | Incremental Volume of End / Building (m³) | 198 | 288 | 378 | 468 | 558 | 648 | 738 | 828 | 918 | 1008 | 1098 | 1188 | 1278 | 1368 | 1458 | 1548 | 1638
|  | Calculated Re-Entry Section (Hrs) | 0.08 | 0.12929 | 0.18855 | 0.25938 | 0.34363 | 0.44339 | 0.56108 | 0.69945 | 0.86164 | 1.0512 | 1.2723 | 1.5296 | 1.8283 | 2.1745 | 2.5751 | 3.0378 | 3.5716
|  | Calculated Re-Entry over distance (Hrs) | 0.049293 | 0.059259 | 0.070832 | 0.084244 | 0.099763 | 0.11769 | 0.13837 | 0.16219 | 0.1896 | 0.22109 | 0.25725 | 0.29871 | 0.3462 | 0.40056 | 0.46273 | 0.53377 | -3.5716
|  | Calculated Re-Entry over distance (Minutes) | 2 | 3 | 4 | 5 | 5 | 7 | 8 | 9 | 11 | 13 | 15 | 17 | 20 | 24 | 27 | 32 | 25
|  | End 1 Cumulative (Minutes) | 2 | 5 | 9 | 14 | 19 | 26 | 34 | 43 | 54 | 67 | 82 | 99 | 119 | 143 | 170 | 202 | 227
|  | TOTAL Re-Entry (Minutes) | 3 | 7 | 12 | 19 | 26 | 36 | 47 | 60 | 76 | 95 | 117 | 142 | 171 | 206 | 245 | 291 | 332
Note: 1 cubic foot per minute = 0.000471947443 cubic meters / second
Air Change Ventilation Guidelines
Mean (All)
|  |  |  | 4 | 8 |  | 6
|  |  |  | 20 | 30 |  | 25
|  |  |  | 3 | 4 |  | 3.5
|  |  |  | 10 | 12 |  | 11
|  |  |  | 5 | 10 |  | 7.5
|  |  |  | 8 | 12 |  | 10
|  |  |  | 6 | 8 |  | 7
|  |  |  | 3 | 5 |  | 4
|  |  |  | 6 | 8 |  | 7
|  |  |  | 6 | 12 |  | 9
|  |  |  | 10 | 15 |  | 12.5
|  |  |  | 4 | 6 |  | 5
|  |  |  | 15 | 30 |  | 22.5
|  |  |  | 8 | 12 |  | 10
|  |  |  | 15 | 30 |  | 22.5
|  |  |  | 8 | 15 |  | 11.5
|  |  |  | 3 | 5 |  | 4
|  |  |  | 4 | 8 |  | 6
|  |  |  | 10 | 15 |  | 12.5
|  |  |  | 10 | 12 |  | 11
|  |  |  | 6 | 10 |  | 8
|  |  |  | 2 | 4 |  | 3
|  |  |  | 7.5455 | 12.3182 |  | 9.9318
10.119
Whirly Bird Size and Extraction
. | Size | Description | 0.3 22: Extraction Rate m³/hr; m/s 32: Area m²; m/s 42: Extraction Rate m³/s
SU01 | 250mm | Supavent (polycarbonate) | 0.3 22: 1229; m/s 32: +/- 35m²; m/s 42: 0.34139
CY01 | 250mm | Cyclovent 250mm galvanised | 0.3 22: 1350; m/s 32: +/- 45m²; m/s 42: 0.375
CY02 | 250mm | Cyclovent 250mm aluminium | 0.3 22: 1350; m/s 32: +/- 45m²; m/s 42: 0.375
CY03 | 250mm | Cyclovent 250mm zinc aluminium | 0.3 22: 1350; m/s 32: +/- 45m²; m/s 42: 0.375
CY04 | 250mm | Cyclovent 250mm chromadek | 0.3 22: 1350; m/s 32: +/- 45m²; m/s 42: 0.375
WH01 | 300mm | Whirlybird (galvanized) | 0.3 22: 924; m/s 32: +/- 30m²; m/s 42: 0.25667
WH02 | 300mm | Whirlybird (aluminium) | 0.3 22: 924; m/s 32: +/- 30m²; m/s 42: 0.25667
WH03 | 350mm | Whirlybird (aluminium) | 0.3 22: 1155; m/s 32: +/- 35m²; m/s 42: 0.32083
CY05 | 450mm | Cyclovent 450mm galvanised | 0.3 22: 5100; m/s 32: +/- 100m²; m/s 42: 1.4167
CY06 | 450mm | Cyclovent 450mm aluminium | 0.3 22: 5100; m/s 32: +/- 100m²; m/s 42: 1.4167
CY07 | 450mm | Cyclovent 450mm zinc aluminium | 0.3 22: 5100; m/s 32: +/- 100m²; m/s 42: 1.4167
CY08 | 450mm | Cyclovent 450mm chromadek | 0.3 22: 5100; m/s 32: +/- 100m²; m/s 42: 1.4167
LP01 | 500mm | LP Vent (aluminium alloy) | 0.3 22: 4695; m/s 32: +/- 90m²; m/s 42: 1.3042
TW01 | 500mm | Twister (galvanized) | 0.3 22: 4695; m/s 32: +/- 90m²; m/s 42: 1.3042
TW02 | 500mm | Twister (aluminium) | 0.3 22: 4695; m/s 32: +/- 90m²; m/s 42: 1.3042
TW03 | 500mm | Twister (zinc aluminium) | 0.3 22: 4695; m/s 32: +/- 90m²; m/s 42: 1.3042
LP02 | 600mm | LP Vent (aluminum alloy) | 0.3 22: 6150; m/s 32: +/- 120m²; m/s 42: 1.7083
TW04 | 610mm | Twister (galvanized) | 0.3 22: 6150; m/s 32: +/- 120m²; m/s 42: 1.7083
TW05 | 610mm | Twister (aluminium) | 0.3 22: 6150; m/s 32: +/- 120m²; m/s 42: 1.7083
TW06 | 610mm | Twister (zinc-aluminium) | 0.3 22: 6150; m/s 32: +/- 120m²; m/s 42: 1.7083
CY09 | 610mm | Cyclovent 610mm galvanised | 0.3 22: 7690; m/s 32: +/- 150m²; m/s 42: 2.1361
CY10 | 610mm | Cyclovent 610mm aluminium | 0.3 22: 7690; m/s 32: +/- 150m²; m/s 42: 2.1361
CY11 | 610mm | Cyclovent 610mm zinc aluminium | 0.3 22: 7690; m/s 32: +/- 150m²; m/s 42: 2.1361
CY12 | 610mm | Cyclovent 610mm chromadek | 0.3 22: 7690; m/s 32: +/- 150m²; m/s 42: 2.1361
BTU Calculator | bar: 0.3 22 to m/s 32
|  | Length of End / Building | 0.3 22: 8.8; m/s 32: m; m/s 42: 52.8; m/s 52: m²
|  | Width of End / Building | 0.3 22: 6; m/s 32: m
|  | Room Area BTU = | 0.3 22: 17793.6; m/s 32: BTU; m/s 42: Note *: Calculation for a normal height building of ±3m x answer
|  | Window Size and Position | 0.3 22: North; m/s 32: South
|  |  | Height (m) | Width (m) | North | South
|  | Window 1 | 0.3 22: 1.2; m/s 32: 2; m/s 42: 1; m/s 72: Note: ADD a "1" to the applicable scenario
|  | Window 2 | 0.3 22: 1.2; m/s 32: 2.5; m/s 42: 1
Window 3 | bar: 0.3 22 to m/s 62
Window 4 | bar: 0.3 22 to m/s 62
Window 5 | bar: 0.3 22 to m/s 62
|  | Blinds Installed ? | 0.3 22: 0; m/s 32: 1; m/s 42: Note **: ADD a "1" to the applicable scenario
|  | Window BTU Load | 0.3 22: 4698; m/s 32: BTU
|  | Number of people in building | 0.3 22: 6; m/s 32: People
|  | BTU Heatload factor per person | 0.3 22: 400; m/s 32: BTU; m/s 42: Note: The source of this Calculator uses 400BTU, this Equates to 117W per person which a bit high
|  | Total Occupant BTU | 0.3 22: 2400; m/s 32: BTU; m/s 42: *** Note: typically a resting person will emit 70 - 100W of heat; m/s 122: =; m/s 132: 240 - 340 BTU
|  | Equipment wattage (All Combined) | 0.3 22: 1000; m/s 32: Watt; m/s 42: A working person will emit 180 - 200W of heat; m/s 122: =; m/s 132: 615 - 683 BTU
|  | Equipment BTU | 0.3 22: 3500; m/s 32: BTU; m/s 42: A hard working person will emit 200 - 240W of heat; m/s 122: =; m/s 132: 683 - 820 BTU
|  | Lighting wattage (All Combined) | 0.3 22: 120; m/s 32: Watt
|  | Equipment BTU | 0.3 22: 510; m/s 32: BTU
|  | Thus Total BTU Required : | 0.3 22: 28901.6; m/s 32: BTU
|  | Thus Total kW Load : | 0.3 22: 8.4702; m/s 32: kW; m/s 42: Note ****: 1KW is equivalent to 3412BTUs
Note on D33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on E33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on F33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on G33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on H33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on I33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on J33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on K33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on L33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on M33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on N33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on O33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on P33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on Q33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on R33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on S33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on T33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on U33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on V33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on W33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on X33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on Y33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on Z33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on AA33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on AB33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on AC33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on AD33: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on D46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on E46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on F46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on G46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on H46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on I46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on J46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on K46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on L46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on M46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on N46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on O46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on P46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on Q46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on R46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on S46: Fan Volume if RED = SUB STANDARD Delivery Volume
Note on D129: No: Add a "1"
Note on E129: Yes: Add a "1"
Note on D132: Johan van Sittert: See ***Note:...

## Re Entry Table
Re-Entry Table | [12 empty] | Back to INDEX
Note: this can be issued to mining as a quick reference table
Minimum air Required |  | 21 |  | m³/s
|  | H | W
End Size: |  | 5.5 | 6
Airchanges Required |  | 8
Velocity measured |  | 0.25 |  | 0.3 |  | 0.35 |  | 0.4 |  | 0.45 |  | 0.5 |  | 0.55 |  | 0.6 |  | 0.65 |  | 0.7 |  | 0.75 |  | 0.8 |  | 0.85 |  | 0.9 |  | 0.95 |  | 1 |  | 1.05 |  | 1.1 |  | 1.15 |  | 1.2 |  | 1.25 |  | 1.3 |  | 1.35 |  | 1.4
Qty Delivered |  | 8.25 |  | 9.9 |  | 11.55 |  | 13.2 |  | 14.85 |  | 16.5 |  | 18.15 |  | 19.8 |  | 21.45 |  | 23.1 |  | 24.75 |  | 26.4 |  | 28.05 |  | 29.7 |  | 31.35 |  | 33 |  | 34.65 |  | 36.3 |  | 37.95 |  | 39.6 |  | 41.25 |  | 42.9 |  | 44.55 |  | 46.2
Re Entry Hrs / Min |  | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min | Hr | Min
End Length (m) | 320 | 2 | 50 | 2 | 22 | 2 | 1 | 1 | 46 | 1 | 34 | 1 | 25 | 1 | 17 | 1 | 11 | 1 | 5 | 1 | 0 | 0 | 56 | 0 | 53 | 0 | 50 | 0 | 47 | 0 | 44 | 0 | 42 | 0 | 40 | 0 | 38 | 0 | 37 | 0 | 35 | 0 | 34 | 0 | 32 | 0 | 31 | 0 | 30
| 300 | 2 | 40 | 2 | 13 | 1 | 54 | 1 | 40 | 1 | 28 | 1 | 20 | 1 | 12 | 1 | 6 | 1 | 1 | 0 | 57 | 0 | 53 | 0 | 50 | 0 | 47 | 0 | 44 | 0 | 42 | 0 | 40 | 0 | 38 | 0 | 36 | 0 | 34 | 0 | 33 | 0 | 32 | 0 | 30 | 0 | 29 | 0 | 28
| 280 | 2 | 29 | 2 | 4 | 1 | 46 | 1 | 33 | 1 | 22 | 1 | 14 | 1 | 7 | 1 | 2 | 0 | 57 | 0 | 53 | 0 | 49 | 0 | 46 | 0 | 43 | 0 | 41 | 0 | 39 | 0 | 37 | 0 | 35 | 0 | 33 | 0 | 32 | 0 | 31 | 0 | 29 | 0 | 28 | 0 | 27 | 0 | 26
| 260 | 2 | 18 | 1 | 55 | 1 | 39 | 1 | 26 | 1 | 17 | 1 | 9 | 1 | 3 | 0 | 57 | 0 | 53 | 0 | 49 | 0 | 46 | 0 | 43 | 0 | 40 | 0 | 38 | 0 | 36 | 0 | 34 | 0 | 33 | 0 | 31 | 0 | 30 | 0 | 28 | 0 | 27 | 0 | 26 | 0 | 25 | 0 | 24
| 240 | 2 | 8 | 1 | 46 | 1 | 31 | 1 | 20 | 1 | 11 | 1 | 4 | 0 | 58 | 0 | 53 | 0 | 49 | 0 | 45 | 0 | 42 | 0 | 40 | 0 | 37 | 0 | 35 | 0 | 33 | 0 | 32 | 0 | 30 | 0 | 29 | 0 | 27 | 0 | 26 | 0 | 25 | 0 | 24 | 0 | 23 | 0 | 22
| 220 | 1 | 57 | 1 | 37 | 1 | 23 | 1 | 13 | 1 | 5 | 0 | 58 | 0 | 53 | 0 | 48 | 0 | 45 | 0 | 41 | 0 | 39 | 0 | 36 | 0 | 34 | 0 | 32 | 0 | 30 | 0 | 29 | 0 | 27 | 0 | 26 | 0 | 25 | 0 | 24 | 0 | 23 | 0 | 22 | 0 | 21 | 0 | 20
| 200 | 1 | 46 | 1 | 28 | 1 | 16 | 1 | 6 | 0 | 59 | 0 | 53 | 0 | 48 | 0 | 44 | 0 | 41 | 0 | 38 | 0 | 35 | 0 | 33 | 0 | 31 | 0 | 29 | 0 | 28 | 0 | 26 | 0 | 25 | 0 | 24 | 0 | 23 | 0 | 22 | 0 | 21 | 0 | 20 | 0 | 19 | 0 | 19
| 180 | 1 | 36 | 1 | 20 | 1 | 8 | 1 | -1 | 0 | 53 | 0 | 48 | 0 | 43 | 0 | 40 | 0 | 36 | 0 | 34 | 0 | 32 | 0 | 30 | 0 | 28 | 0 | 26 | 0 | 25 | 0 | 24 | 0 | 22 | 0 | 21 | 0 | 20 | 0 | 20 | 0 | 19 | 0 | 18 | 0 | 17 | 0 | 17
| 160 | 1 | 25 | 1 | 11 | 1 | 0 | 0 | 53 | 0 | 47 | 0 | 42 | 0 | 38 | 0 | 35 | 0 | 32 | 0 | 30 | 0 | 28 | 0 | 26 | 0 | 25 | 0 | 23 | 0 | 22 | 0 | 21 | 0 | 20 | 0 | 19 | 0 | 18 | 0 | 17 | 0 | 17 | 0 | 16 | 0 | 15 | 0 | 15
| 140 | 1 | 14 | 1 | 2 | 0 | 53 | 0 | 46 | 0 | 41 | 0 | 37 | 0 | 33 | 0 | 31 | 0 | 28 | 0 | 26 | 0 | 24 | 0 | 23 | 0 | 21 | 0 | 20 | 0 | 19 | 0 | 18 | 0 | 17 | 0 | 16 | 0 | 16 | 0 | 15 | 0 | 14 | 0 | 14 | 0 | 13 | 0 | 13
| 120 | 1 | 4 | 0 | 53 | 0 | 45 | 0 | 40 | 0 | 35 | 0 | 32 | 0 | 29 | 0 | 26 | 0 | 24 | 0 | 22 | 0 | 21 | 0 | 20 | 0 | 18 | 0 | 17 | 0 | 16 | 0 | 16 | 0 | 15 | 0 | 14 | 0 | 13 | 0 | 13 | 0 | 12 | 0 | 12 | 0 | 11 | 0 | 11
| 100 | 0 | 53 | 0 | 44 | 0 | 38 | 0 | 33 | 0 | 29 | 0 | 26 | 0 | 24 | 0 | 22 | 0 | 20 | 0 | 19 | 0 | 17 | 0 | 16 | 0 | 15 | 0 | 14 | 0 | 14 | 0 | 13 | 0 | 12 | 0 | 12 | 0 | 11 | 0 | 11 | 0 | 10 | 0 | 10 | 0 | 9 | 0 | 9
| 80 | 0 | 42 | 0 | 35 | 0 | 30 | 0 | 26 | 0 | 23 | 0 | 21 | 0 | 19 | 0 | 17 | 0 | 16 | 0 | 15 | 0 | 14 | 0 | 13 | 0 | 12 | 0 | 11 | 0 | 11 | 0 | 10 | 0 | 10 | 0 | 9 | 0 | 9 | 0 | 8 | 0 | 8 | 0 | 8 | 0 | 7 | 0 | 7
| 60 | 0 | 32 | 0 | 26 | 0 | 22 | 0 | 20 | 0 | 17 | 0 | 16 | 0 | 14 | 0 | 13 | 0 | 12 | 0 | 11 | 0 | 10 | 0 | 10 | 0 | 9 | 0 | 8 | 0 | 8 | 0 | 8 | 0 | 7 | 0 | 7 | 0 | 6 | 0 | 6 | 0 | 6 | 0 | 6 | 0 | 5 | 0 | 5
| 40 | 0 | 21 | 0 | 17 | 0 | 15 | 0 | 13 | 0 | 11 | 0 | 10 | 0 | 9 | 0 | 8 | 0 | 8 | 0 | 7 | 0 | 7 | 0 | 6 | 0 | 6 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 3 | 0 | 3
| 20 | 0 | 10 | 0 | 8 | 0 | 7 | 0 | 6 | 0 | 5 | 0 | 5 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 1
|  | 2.8444 |  | 2.3704 |  | 2.0317 |  | 1.7778 |  | 1.5802 |  | 1.4222 |  | 1.2929 |  | 1.1852 |  | 1.094 |  | 1.0159 |  | 0.94815 |  | 0.88889 |  | 0.8366 |  | 0.79012 |  | 0.74854 |  | 0.71111 |  | 0.67725 |  | 0.64646 |  | 0.61836 |  | 0.59259 |  | 0.56889 |  | 0.54701 |  | 0.52675 |  | 0.50794
|  | 2.6667 |  | 2.2222 |  | 1.9048 |  | 1.6667 |  | 1.4815 |  | 1.3333 |  | 1.2121 |  | 1.1111 |  | 1.0256 |  | 0.95238 |  | 0.88889 |  | 0.83333 |  | 0.78431 |  | 0.74074 |  | 0.70175 |  | 0.66667 |  | 0.63492 |  | 0.60606 |  | 0.57971 |  | 0.55556 |  | 0.53333 |  | 0.51282 |  | 0.49383 |  | 0.47619
|  | 2.4889 |  | 2.0741 |  | 1.7778 |  | 1.5556 |  | 1.3827 |  | 1.2444 |  | 1.1313 |  | 1.037 |  | 0.95726 |  | 0.88889 |  | 0.82963 |  | 0.77778 |  | 0.73203 |  | 0.69136 |  | 0.65497 |  | 0.62222 |  | 0.59259 |  | 0.56566 |  | 0.54106 |  | 0.51852 |  | 0.49778 |  | 0.47863 |  | 0.46091 |  | 0.44444
|  | 2.3111 |  | 1.9259 |  | 1.6508 |  | 1.4444 |  | 1.284 |  | 1.1556 |  | 1.0505 |  | 0.96296 |  | 0.88889 |  | 0.8254 |  | 0.77037 |  | 0.72222 |  | 0.67974 |  | 0.64198 |  | 0.60819 |  | 0.57778 |  | 0.55026 |  | 0.52525 |  | 0.50242 |  | 0.48148 |  | 0.46222 |  | 0.44444 |  | 0.42798 |  | 0.4127
|  | 2.1333 |  | 1.7778 |  | 1.5238 |  | 1.3333 |  | 1.1852 |  | 1.0667 |  | 0.9697 |  | 0.88889 |  | 0.82051 |  | 0.7619 |  | 0.71111 |  | 0.66667 |  | 0.62745 |  | 0.59259 |  | 0.5614 |  | 0.53333 |  | 0.50794 |  | 0.48485 |  | 0.46377 |  | 0.44444 |  | 0.42667 |  | 0.41026 |  | 0.39506 |  | 0.38095
|  | 1.9556 |  | 1.6296 |  | 1.3968 |  | 1.2222 |  | 1.0864 |  | 0.97778 |  | 0.88889 |  | 0.81481 |  | 0.75214 |  | 0.69841 |  | 0.65185 |  | 0.61111 |  | 0.57516 |  | 0.54321 |  | 0.51462 |  | 0.48889 |  | 0.46561 |  | 0.44444 |  | 0.42512 |  | 0.40741 |  | 0.39111 |  | 0.37607 |  | 0.36214 |  | 0.34921
|  | 1.7778 |  | 1.4815 |  | 1.2698 |  | 1.1111 |  | 0.98765 |  | 0.88889 |  | 0.80808 |  | 0.74074 |  | 0.68376 |  | 0.63492 |  | 0.59259 |  | 0.55556 |  | 0.52288 |  | 0.49383 |  | 0.46784 |  | 0.44444 |  | 0.42328 |  | 0.40404 |  | 0.38647 |  | 0.37037 |  | 0.35556 |  | 0.34188 |  | 0.32922 |  | 0.31746
|  | 1.6 |  | 1.3333 |  | 1.1429 |  | 1 |  | 0.88889 |  | 0.8 |  | 0.72727 |  | 0.66667 |  | 0.61538 |  | 0.57143 |  | 0.53333 |  | 0.5 |  | 0.47059 |  | 0.44444 |  | 0.42105 |  | 0.4 |  | 0.38095 |  | 0.36364 |  | 0.34783 |  | 0.33333 |  | 0.32 |  | 0.30769 |  | 0.2963 |  | 0.28571
|  | 1.4222 |  | 1.1852 |  | 1.0159 |  | 0.88889 |  | 0.79012 |  | 0.71111 |  | 0.64646 |  | 0.59259 |  | 0.54701 |  | 0.50794 |  | 0.47407 |  | 0.44444 |  | 0.4183 |  | 0.39506 |  | 0.37427 |  | 0.35556 |  | 0.33862 |  | 0.32323 |  | 0.30918 |  | 0.2963 |  | 0.28444 |  | 0.2735 |  | 0.26337 |  | 0.25397
|  | 1.2444 |  | 1.037 |  | 0.88889 |  | 0.77778 |  | 0.69136 |  | 0.62222 |  | 0.56566 |  | 0.51852 |  | 0.47863 |  | 0.44444 |  | 0.41481 |  | 0.38889 |  | 0.36601 |  | 0.34568 |  | 0.32749 |  | 0.31111 |  | 0.2963 |  | 0.28283 |  | 0.27053 |  | 0.25926 |  | 0.24889 |  | 0.23932 |  | 0.23045 |  | 0.22222
|  | 1.0667 |  | 0.88889 |  | 0.7619 |  | 0.66667 |  | 0.59259 |  | 0.53333 |  | 0.48485 |  | 0.44444 |  | 0.41026 |  | 0.38095 |  | 0.35556 |  | 0.33333 |  | 0.31373 |  | 0.2963 |  | 0.2807 |  | 0.26667 |  | 0.25397 |  | 0.24242 |  | 0.23188 |  | 0.22222 |  | 0.21333 |  | 0.20513 |  | 0.19753 |  | 0.19048
|  | 0.88889 |  | 0.74074 |  | 0.63492 |  | 0.55556 |  | 0.49383 |  | 0.44444 |  | 0.40404 |  | 0.37037 |  | 0.34188 |  | 0.31746 |  | 0.2963 |  | 0.27778 |  | 0.26144 |  | 0.24691 |  | 0.23392 |  | 0.22222 |  | 0.21164 |  | 0.20202 |  | 0.19324 |  | 0.18519 |  | 0.17778 |  | 0.17094 |  | 0.16461 |  | 0.15873
|  | 0.71111 |  | 0.59259 |  | 0.50794 |  | 0.44444 |  | 0.39506 |  | 0.35556 |  | 0.32323 |  | 0.2963 |  | 0.2735 |  | 0.25397 |  | 0.23704 |  | 0.22222 |  | 0.20915 |  | 0.19753 |  | 0.18713 |  | 0.17778 |  | 0.16931 |  | 0.16162 |  | 0.15459 |  | 0.14815 |  | 0.14222 |  | 0.13675 |  | 0.13169 |  | 0.12698
|  | 0.53333 |  | 0.44444 |  | 0.38095 |  | 0.33333 |  | 0.2963 |  | 0.26667 |  | 0.24242 |  | 0.22222 |  | 0.20513 |  | 0.19048 |  | 0.17778 |  | 0.16667 |  | 0.15686 |  | 0.14815 |  | 0.14035 |  | 0.13333 |  | 0.12698 |  | 0.12121 |  | 0.11594 |  | 0.11111 |  | 0.10667 |  | 0.10256 |  | 0.098765 |  | 0.095238
|  | 0.35556 |  | 0.2963 |  | 0.25397 |  | 0.22222 |  | 0.19753 |  | 0.17778 |  | 0.16162 |  | 0.14815 |  | 0.13675 |  | 0.12698 |  | 0.11852 |  | 0.11111 |  | 0.10458 |  | 0.098765 |  | 0.093567 |  | 0.088889 |  | 0.084656 |  | 0.080808 |  | 0.077295 |  | 0.074074 |  | 0.071111 |  | 0.068376 |  | 0.065844 |  | 0.063492
|  | 0.17778 |  | 0.14815 |  | 0.12698 |  | 0.11111 |  | 0.098765 |  | 0.088889 |  | 0.080808 |  | 0.074074 |  | 0.068376 |  | 0.063492 |  | 0.059259 |  | 0.055556 |  | 0.052288 |  | 0.049383 |  | 0.046784 |  | 0.044444 |  | 0.042328 |  | 0.040404 |  | 0.038647 |  | 0.037037 |  | 0.035556 |  | 0.034188 |  | 0.032922 |  | 0.031746
Note on B7: Velocity measured one pipe length back from discharge

## Noise Log ave
| Courtesy of : Julize Hasenbroek Adoption Team Manager: Noise |  |  |  | Back to INDEX
| Actual readings |  |  | 55577997671.0904
1 | 104.3 | 26915348039.2692
2 | 89.8 | 954992586.0214 |  | 9262999611.8484
3 | 90.5 | 1122018454.302
4 | 84.7 | 295120922.6666 | Log Avg | 99.6675
5 | 102.4 | 17378008287.4938
6 | 99.5 | 8912509381.3375
7 |  |  | Log Avg | 99.6675
8
9
Note on F11: Single Formula

## Cold Stress
Back to INDEX
Cold Stress (WCET) OLD Formulae
Where
Air Temperature | -10 | °C (DB)
Airspeed | 2.5 | m/s Velocity
Wind Chill Eq. Temp. | -13.3584 | °C (WCET)
Speed = | 9 | km/hr
Cold Stress (WCET) Steadman Formulae
Where
Air Temperature | -10 | °C (DB)
Airspeed | 2.5 | m/s Velocity
Wind Chill Eq. Temp. | -11.68 | °C (WCET)
Speed = | 9 | km/hr
Cold Stress (WCET) Table Formulae 1
Where
Air Temperature | -10 | °C (DB)
Airspeed | 2.5 | m/s Velocity
Airspeed | 9 | km/h Velocity
Wind Chill Eq. Temp. | -14.8903 | °C (WCET)
Cold Stress (WCET) Table Formulae 2
Where
Air Temperature | -10 | °C (DB)
Airspeed | 2.5 | m/s Velocity
Wind Chill Eq. Temp. | -14.8903 | °C (WCET)
Speed = | 9 | km/hr
COLD STRESS RELATED AIR TEMPERATURES Report
Table 17.2 Categorisation of the thermal environment
[7 empty] | Date | 41498
[10 empty] | Thermal zone | Environment (°C) | Health risk level | Category/action
TEMPERATURES TAKEN ON SURFACE AND IN THE SHAFT, AT THE POTENTIALLY COLDEST WORKING PLACES | [5 empty] | Steadman | Table 2 | 3.1 Table method |  | Heat | DB > 32,5 | Significant to | A, B or Cb
WORKING PLACE | WET BULB | DRY BULB | VELOCITY | VELOCITY | E.C.T.* | E.C.T.* | E.C.T.* | E.C.T.* | TIME |  | GT > 32,5 | unacceptable | Formal HSMc
| OC | OC | m/s | km/h | [6 empty] | WB > 27,5 |  | EHSId optional
| -0.5 | 1 | 1 | 3.6 | 4.7604 | 1.2589 | 0.27194 | 0.27194 |  |  | DB > 32,0 | Potential Db | Formal COP
| -0.5 | 2 | 2 | 7.2 | 1.2234 | 1.1696 | -0.1426 | -0.1426 |  |  | GT > 32,0
| -0.5 | 3 | 3 | 10.8 | -0.71666 | 1.1421 | 0.086879 | 0.086879 |  |  | WB > 25,0
| -0.5 | 3 | 4 | 14.4 | -3.0027 | 0.1224 | -0.61487 | -0.61487 |  | Thermoneutral | DB ≤ 32,0 | No risk | Professional discretion
| -0.5 | 3 | 5 | 18 | -4.8548 | -0.8725 | -1.1819 | -1.1819 |  |  | GT ≤ 32,0
| -0.5 | 3 | 10 | 36 | -10.6562 | -5.475 | -3.078 | -3.078 |  |  | WB ≤ 25,0
ECTe ≤ 10,0
[10 empty] | Cold | ECT < 10,0 | Potential | Cb Formal COP
REMARKS | [10 empty] | ECT < 5,0 | Significant | Bb Formal CSMc
Working places with an E.C.T. (Equivalent Chill Temperature) of less than 5.0 deg C, require a plan of action to protect the people working in these conditions. (i.e. keep them warm) | [10 empty] | ECT ≤ 30,0 | Severe to unacceptable | Ab Stop work; evacuate
Please ensure that workers are provided with the necessary protective clothing and PPE, (Suitable Socks and Gloves, Beanies and Freezer Suits.)
[5 empty] | Thermal zone | Environment (°C) | Health risk level | Category / Action
[5 empty] | Cold | ECT < 10,0 | Potential | Cb Formal COP |  | aDME Guideline on Thermal Stress, Figure 17.1
CHIEF OCCUPATIONAL HYGIENIST | [5 empty] | ECT < 5,0 | Significant | Bb Formal CSMc |  | bSAMOHP Codebook categorisation system (Section 2.2)
[6 empty] | ECT ≤ 30,0 | Severe to unacceptable | Ab Stop work; evacuate |  | cHeat Stress/Cold Stress Management (See DME Guideline on Thermal Stress)
dEmergency Heat Stress Index (See DME Guideline on Thermal Stress: Annex 10)
eEffective chill temperature
ENGINEERING MANAGER | [9 empty] | Note: There are slight discrepancies between the action levels and actions specified in Regulation 9.2
(2)(b) and those associated with Category D (‘Heat’) and C (‘Cold’) in the SAMOHP Codebook. A
‘system of occupational hygiene measurements’ can only be established and maintained within the
context of a COP (DME Guideline on Thermal Stress: Part A, Section 5).
PRODUCTION MANAGER | [9 empty] | By contrast, the only practical index addressing cold stress is the wind chill index (WCI),
which expresses the combined effect of air temperature and air movement (speed; velocity) in
|  | Requirements in terms of the Mine Health and Safety Act Sect 9.2 (2)(b) | [7 empty] | terms of and equivalent cooling (chill) temperature (ECT). The relevant reference is ISO TR
11079 (Table 17.3). Cold stress must be reported as ‘ECT’ according to Regulation 9.2(7).
MINE MANAGER |  | * E.C.T. | EQUIVALENT CHILL TEMPERATURE
THIS IS AN OLD FORMULAE (2001). IT TIES IN WITH THE MVS DATA BOOK TABLE
[5 empty] | WCET | = | Wind Chill Equivalent Temperature
[5 empty] | v | = | Wind speed (m/s)
[5 empty] | T | = | air temperature, dry bulb (oC)
or
Wind Chill = 35.74 + 0.6215T "“ 35.75(V^0.16) + 0.4275T(V^0.16)
T is the air temperature in degrees Fahrenheit, and V is the wind speed in miles per hour.
[14 empty] | 1 | 2
THIS PICTURE IS FROM COP
OLD FORMULAE
NEW FORMULAE
13.12
NEW FORMULAE
0

## SCP - Kata - Vel
Development | [5 empty] | Back to INDEX
Formulae
[5 empty] | Observation point | Kata Factor | Kata Stopwatch Time | wet kata reading | BP Inside Chamber kPa | °C W/Bulb | °C D/Bulb | θ 36.5 - WB temperature [°C] | Calculated air velocity [m/s] | Mean Velocity m/s | Humidity % | Mean Humidity % | Specific Cooling Power (SCP W/m²) | Mean SCP W/m²
H | = | Kata Correction Factor | 178 |  | 1 | 268 | 20.35 | 13.1695 | 90.86 | 28 | 30.5 | 8.5 | 0.72141 | 0.68069 | 83.219 | 82.6614 | 295 | 287.6667
| = | Time | 5.64 |  | 2 | 268 | 23.25 | 11.5269 | 90.86 | 28 | 30.5 | 8.5 | 0.43047 |  | 83.219 |  | 270
[5 empty] | 3 | 268 | 21.1 | 12.7014 | 90.86 | 28.1 | 30.5 | 8.4 | 0.65946 |  | 83.8584 |  | 286
Where H = 0.7θ+θ√V |  |  |  |  | 4 | 268 | 20.76 | 12.9094 | 90.86 | 28.2 | 31 | 8.3 | 0.73163 |  | 81.4731 |  | 291
Thus: V = ((H-(0.7θ)) / θ)^2 |  |  |  |  | 5 | 268 | 19.7 | 13.6041 | 90.86 | 28.3 | 31 | 8.2 | 0.91974 |  | 82.0995 |  | 302
H | = | wet kata reading | 31.5603 | Input | 6 | 268 | 21.96 | 12.204 | 90.86 | 28.3 | 31 | 8.2 | 0.62141 |  | 82.0995 |  | 282
W/Bulb | = | °C | 21 | Input
θ | = | 36.5 - wet bulb temperature [°C] | 15.5
[7 empty] | 5.14 | 5.64
V | = | air velocity [m/s] | 1.7853 | m/s
SCP | = | Specific Cooling Power | 467 | W/m²
[5 empty] | Observation point | Kata Factor | Kata Stopwatch Time | wet kata reading | BP kPa | °C W/Bulb | °C D/Bulb | θ 36.5 - WB temperature [°C] | Calculated air velocity [m/s] | Mean Velocity m/s | Humidity % | Mean Humidity % | Specific Cooling Power (SCP W/m²) | Mean SCP W/m²
[5 empty] | 1 | 268 | 25.7 | 10.428 | 90.86 | 28.1 | 30.3 | 8.4 | 0.29315 | 0.33383 | 85.0943 | 85.0943 | 245 | 253.6667
Stoping |  |  |  |  | 2 | 268 | 25.39 | 10.5553 | 90.86 | 28.1 | 30.3 | 8.4 | 0.30979 |  | 85.0943 |  | 258
T | = | Wet bulb temperature [°C] | 24.8 | Input | 3 | 268 | 24.16 | 11.0927 | 90.86 | 28.1 | 30.3 | 8.4 | 0.3851 |  | 85.0943 |  | 258
V | = | air velocity [m/s] | 0.28 | Input | 4 | 268 | 24.29 | 11.0333 | 90.86 | 28.1 | 30.3 | 8.4 | 0.37637 |  | 85.0943 |  | 258
SCP | = | Specific Cooling Power | 304 | W/m² | 5 | 268 | 24.12 | 11.1111 | 90.86 | 28.1 | 30.3 | 8.4 | 0.38782 |  | 85.0943 |  | 258
[5 empty] | 6 | 268 | 26.57 | 10.0866 | 90.86 | 28.1 | 30.3 | 8.4 | 0.25078 |  | 85.0943 |  | 245
Wet KATA
H = 0.7θ + θ√V
(θ 3 = 36.5 - wet bulb temperature [°C])
|  | Wet bulb | 28.15 | °C
|  | Velocity | 0.769 | m/s
|  | KATA | 13.1673 | mC/m²/s

## WP
Velocity | 1.7853 | 0.28
Temperature | 21 | 24.8
SCP | 467 | 304
Work Performance | 173% | 112.6%
1 | [6 empty] | 2 | [5 empty] | 3 | [5 empty] | 4 | [5 empty] | 5 |  |  |  | 6 | 7 | 8 | 9 | 10
Work Performance Chart at 240 W/m²
| 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.2 | 2.4 | 2.6 | 2.8 | 3 | 3.5 | 4 | 4.5
20 | 156.6667 | 156.6667 | 158.75 | 164.1667 | 168.75 | 172.9167 | 176.6667 | 180 | 182.9167 | 185.8333 | 188.3333 | 190.4167 | 192.5 | 194.5833 | 196.6667 | 198.3333 | 200 | 201.6667 | 202.9167 | 204.5833 | 207.0833 | 209.5833 | 211.6667 | 213.75 | 215.4167 | 219.5833 | 222.9167 | 225.8333
20.1 | 156.25 | 156.25 | 158.3333 | 163.75 | 168.3333 | 172.5 | 176.25 | 179.5833 | 182.5 | 185.4167 | 187.9167 | 190 | 192.0833 | 194.1667 | 196.25 | 197.9167 | 199.5833 | 201.25 | 202.5 | 204.1667 | 206.6667 | 209.1667 | 211.25 | 213.3333 | 215 | 219.1667 | 222.5 | 225.4167
20.2 | 155.4167 | 155.4167 | 157.5 | 162.9167 | 167.5 | 171.6667 | 175.4167 | 178.75 | 181.6667 | 184.5833 | 187.0833 | 189.1667 | 191.25 | 193.3333 | 195.4167 | 197.0833 | 198.75 | 200.4167 | 201.6667 | 203.3333 | 205.8333 | 208.3333 | 210.4167 | 212.5 | 214.1667 | 218.3333 | 221.6667 | 224.5833
20.3 | 154.5833 | 154.5833 | 156.6667 | 162.0833 | 166.6667 | 170.8333 | 174.5833 | 177.9167 | 180.8333 | 183.75 | 186.25 | 188.3333 | 190.4167 | 192.5 | 194.5833 | 196.25 | 197.9167 | 199.5833 | 200.8333 | 202.5 | 205 | 207.5 | 209.5833 | 211.6667 | 213.3333 | 217.5 | 220.8333 | 223.75
20.4 | 154.1667 | 154.1667 | 156.25 | 161.6667 | 166.25 | 170.4167 | 174.1667 | 177.5 | 180.4167 | 183.3333 | 185.8333 | 187.9167 | 190 | 192.0833 | 194.1667 | 195.8333 | 197.5 | 199.1667 | 200.4167 | 202.0833 | 204.5833 | 207.0833 | 209.1667 | 211.25 | 212.9167 | 217.0833 | 220.4167 | 223.3333
20.5 | 153.75 | 153.75 | 155.8333 | 161.25 | 165.8333 | 170 | 173.75 | 177.0833 | 180 | 182.9167 | 185.4167 | 187.5 | 189.5833 | 191.6667 | 193.75 | 195.4167 | 197.0833 | 198.75 | 200 | 201.6667 | 204.1667 | 206.6667 | 208.75 | 210.8333 | 212.5 | 216.6667 | 220 | 222.9167
20.6 | 152.9167 | 152.9167 | 155 | 160.4167 | 165 | 169.1667 | 172.9167 | 176.25 | 179.1667 | 182.0833 | 184.5833 | 186.6667 | 188.75 | 190.8333 | 192.9167 | 194.5833 | 196.25 | 197.9167 | 199.1667 | 200.8333 | 203.3333 | 205.8333 | 207.9167 | 210 | 211.6667 | 215.8333 | 219.1667 | 222.0833
20.7 | 152.0833 | 152.0833 | 154.1667 | 159.5833 | 164.1667 | 168.3333 | 172.0833 | 175.4167 | 178.3333 | 181.25 | 183.75 | 185.8333 | 187.9167 | 190 | 192.0833 | 193.75 | 195.4167 | 197.0833 | 198.3333 | 200 | 202.5 | 205 | 207.0833 | 209.1667 | 210.8333 | 215 | 218.3333 | 221.25
20.8 | 151.6667 | 151.6667 | 153.75 | 159.1667 | 163.75 | 167.9167 | 171.6667 | 175 | 177.9167 | 180.8333 | 183.3333 | 185.4167 | 187.5 | 189.5833 | 191.6667 | 193.3333 | 195 | 196.6667 | 197.9167 | 199.5833 | 202.0833 | 204.5833 | 206.6667 | 208.75 | 210.4167 | 214.5833 | 217.9167 | 220.8333
20.9 | 151.25 | 151.25 | 153.3333 | 158.75 | 163.3333 | 167.5 | 171.25 | 174.5833 | 177.5 | 180.4167 | 182.9167 | 185 | 187.0833 | 189.1667 | 191.25 | 192.9167 | 194.5833 | 196.25 | 197.5 | 199.1667 | 201.6667 | 204.1667 | 206.25 | 208.3333 | 210 | 214.1667 | 217.5 | 220.4167
21 | 150.4167 | 150.4167 | 152.5 | 157.9167 | 162.5 | 166.6667 | 170.4167 | 173.75 | 176.6667 | 179.5833 | 182.0833 | 184.1667 | 186.25 | 188.3333 | 190.4167 | 192.0833 | 193.75 | 195.4167 | 196.6667 | 198.3333 | 200.8333 | 203.3333 | 205.4167 | 207.5 | 209.1667 | 213.3333 | 216.6667 | 219.5833
21.1 | 149.5833 | 149.5833 | 151.6667 | 157.0833 | 161.6667 | 165.8333 | 169.5833 | 172.9167 | 175.8333 | 178.75 | 181.25 | 183.3333 | 185.4167 | 187.5 | 189.5833 | 191.25 | 192.9167 | 194.5833 | 195.8333 | 197.5 | 200 | 202.5 | 204.5833 | 206.6667 | 208.3333 | 212.5 | 215.8333 | 218.75
21.2 | 149.1667 | 149.1667 | 151.25 | 156.6667 | 161.25 | 165.4167 | 169.1667 | 172.5 | 175.4167 | 178.3333 | 180.8333 | 182.9167 | 185 | 187.0833 | 189.1667 | 190.8333 | 192.5 | 194.1667 | 195.4167 | 197.0833 | 199.5833 | 202.0833 | 204.1667 | 206.25 | 207.9167 | 212.0833 | 215.4167 | 218.3333
21.3 | 148.75 | 148.75 | 150.8333 | 156.25 | 160.8333 | 165 | 168.75 | 172.0833 | 175 | 177.9167 | 180.4167 | 182.5 | 184.5833 | 186.6667 | 188.75 | 190.4167 | 192.0833 | 193.75 | 195 | 196.6667 | 199.1667 | 201.6667 | 203.75 | 205.8333 | 207.5 | 211.6667 | 215 | 217.9167
21.4 | 147.9167 | 147.9167 | 150 | 155.4167 | 160 | 164.1667 | 167.9167 | 171.25 | 174.1667 | 177.0833 | 179.5833 | 181.6667 | 183.75 | 185.8333 | 187.9167 | 189.5833 | 191.25 | 192.9167 | 194.1667 | 195.8333 | 198.3333 | 200.8333 | 202.9167 | 205 | 206.6667 | 210.8333 | 214.1667 | 217.0833
21.5 | 147.0833 | 147.0833 | 149.1667 | 154.5833 | 159.1667 | 163.3333 | 167.0833 | 170.4167 | 173.3333 | 176.25 | 178.75 | 180.8333 | 182.9167 | 185 | 187.0833 | 188.75 | 190.4167 | 192.0833 | 193.3333 | 195 | 197.5 | 200 | 202.0833 | 204.1667 | 205.8333 | 210 | 213.3333 | 216.25
21.6 | 146.6667 | 146.6667 | 148.75 | 154.1667 | 158.75 | 162.9167 | 166.6667 | 170 | 172.9167 | 175.8333 | 178.3333 | 180.4167 | 182.5 | 184.5833 | 186.6667 | 188.3333 | 190 | 191.6667 | 192.9167 | 194.5833 | 197.0833 | 199.5833 | 201.6667 | 203.75 | 205.4167 | 209.5833 | 212.9167 | 215.8333
21.7 | 146.25 | 146.25 | 148.3333 | 153.75 | 158.3333 | 162.5 | 166.25 | 169.5833 | 172.5 | 175.4167 | 177.9167 | 180 | 182.0833 | 184.1667 | 186.25 | 187.9167 | 189.5833 | 191.25 | 192.5 | 194.1667 | 196.6667 | 199.1667 | 201.25 | 203.3333 | 205 | 209.1667 | 212.5 | 215.4167
21.8 | 145.4167 | 145.4167 | 147.5 | 152.9167 | 157.5 | 161.6667 | 165.4167 | 168.75 | 171.6667 | 174.5833 | 177.0833 | 179.1667 | 181.25 | 183.3333 | 185.4167 | 187.0833 | 188.75 | 190.4167 | 191.6667 | 193.3333 | 195.8333 | 198.3333 | 200.4167 | 202.5 | 204.1667 | 208.3333 | 211.6667 | 214.5833
21.9 | 144.5833 | 144.5833 | 146.6667 | 152.0833 | 156.6667 | 160.8333 | 164.5833 | 167.9167 | 170.8333 | 173.75 | 176.25 | 178.3333 | 180.4167 | 182.5 | 184.5833 | 186.25 | 187.9167 | 189.5833 | 190.8333 | 192.5 | 195 | 197.5 | 199.5833 | 201.6667 | 203.3333 | 207.5 | 210.8333 | 213.75
22 | 144.1667 | 144.1667 | 146.25 | 151.6667 | 156.25 | 160.4167 | 164.1667 | 167.5 | 170.4167 | 173.3333 | 175.8333 | 177.9167 | 180 | 182.0833 | 184.1667 | 185.8333 | 187.5 | 189.1667 | 190.4167 | 192.0833 | 194.5833 | 197.0833 | 199.1667 | 201.25 | 202.9167 | 207.0833 | 210.4167 | 213.3333
22.1 | 143.75 | 143.75 | 145.8333 | 151.25 | 155.8333 | 160 | 163.75 | 167.0833 | 170 | 172.9167 | 175.4167 | 177.5 | 179.5833 | 181.6667 | 183.75 | 185.4167 | 187.0833 | 188.75 | 190 | 191.6667 | 194.1667 | 196.6667 | 198.75 | 200.8333 | 202.5 | 206.6667 | 210 | 212.9167
22.2 | 142.9167 | 142.9167 | 145 | 150.4167 | 155 | 159.1667 | 162.9167 | 166.25 | 169.1667 | 172.0833 | 174.5833 | 176.6667 | 178.75 | 180.8333 | 182.9167 | 184.5833 | 186.25 | 187.9167 | 189.1667 | 190.8333 | 193.3333 | 195.8333 | 197.9167 | 200 | 201.6667 | 205.8333 | 209.1667 | 212.0833
22.3 | 142.0833 | 142.0833 | 144.1667 | 149.5833 | 154.1667 | 158.3333 | 162.0833 | 165.4167 | 168.3333 | 171.25 | 173.75 | 175.8333 | 177.9167 | 180 | 182.0833 | 183.75 | 185.4167 | 187.0833 | 188.3333 | 190 | 192.5 | 195 | 197.0833 | 199.1667 | 200.8333 | 205 | 208.3333 | 211.25
22.4 | 141.6667 | 141.6667 | 143.75 | 149.1667 | 153.75 | 157.9167 | 161.6667 | 165 | 167.9167 | 170.8333 | 173.3333 | 175.4167 | 177.5 | 179.5833 | 181.6667 | 183.3333 | 185 | 186.6667 | 187.9167 | 189.5833 | 192.0833 | 194.5833 | 196.6667 | 198.75 | 200.4167 | 204.5833 | 207.9167 | 210.8333
22.5 | 141.25 | 141.25 | 143.3333 | 148.75 | 153.3333 | 157.5 | 161.25 | 164.5833 | 167.5 | 170.4167 | 172.9167 | 175 | 177.0833 | 179.1667 | 181.25 | 182.9167 | 184.5833 | 186.25 | 187.5 | 189.1667 | 191.6667 | 194.1667 | 196.25 | 198.3333 | 200 | 204.1667 | 207.5 | 210.4167
22.6 | 140.4167 | 140.4167 | 142.5 | 147.9167 | 152.5 | 156.6667 | 160.4167 | 163.75 | 166.6667 | 169.5833 | 172.0833 | 174.1667 | 176.25 | 178.3333 | 180.4167 | 182.0833 | 183.75 | 185.4167 | 186.6667 | 188.3333 | 190.8333 | 193.3333 | 195.4167 | 197.5 | 199.1667 | 203.3333 | 206.6667 | 209.5833
22.7 | 139.5833 | 139.5833 | 141.6667 | 147.0833 | 151.6667 | 155.8333 | 159.5833 | 162.9167 | 165.8333 | 168.75 | 171.25 | 173.3333 | 175.4167 | 177.5 | 179.5833 | 181.25 | 182.9167 | 184.5833 | 185.8333 | 187.5 | 190 | 192.5 | 194.5833 | 196.6667 | 198.3333 | 202.5 | 205.8333 | 208.75
22.8 | 139.1667 | 139.1667 | 141.25 | 146.6667 | 151.25 | 155.4167 | 159.1667 | 162.5 | 165.4167 | 168.3333 | 170.8333 | 172.9167 | 175 | 177.0833 | 179.1667 | 180.8333 | 182.5 | 184.1667 | 185.4167 | 187.0833 | 189.5833 | 192.0833 | 194.1667 | 196.25 | 197.9167 | 202.0833 | 205.4167 | 208.3333
22.9 | 138.75 | 138.75 | 140.8333 | 146.25 | 150.8333 | 155 | 158.75 | 162.0833 | 165 | 167.9167 | 170.4167 | 172.5 | 174.5833 | 176.6667 | 178.75 | 180.4167 | 182.0833 | 183.75 | 185 | 186.6667 | 189.1667 | 191.6667 | 193.75 | 195.8333 | 197.5 | 201.6667 | 205 | 207.9167
23 | 137.9167 | 137.9167 | 140 | 145.4167 | 150 | 154.1667 | 157.9167 | 161.25 | 164.1667 | 167.0833 | 169.5833 | 171.6667 | 173.75 | 175.8333 | 177.9167 | 179.5833 | 181.25 | 182.9167 | 184.1667 | 185.8333 | 188.3333 | 190.8333 | 192.9167 | 195 | 196.6667 | 200.8333 | 204.1667 | 207.0833
23.1 | 137.0833 | 137.0833 | 139.1667 | 144.5833 | 149.1667 | 153.3333 | 157.0833 | 160.4167 | 163.3333 | 166.25 | 168.75 | 170.8333 | 172.9167 | 175 | 177.0833 | 178.75 | 180.4167 | 182.0833 | 183.3333 | 185 | 187.5 | 190 | 192.0833 | 194.1667 | 195.8333 | 200 | 203.3333 | 206.25
23.2 | 136.6667 | 136.6667 | 138.75 | 144.1667 | 148.75 | 152.9167 | 156.6667 | 160 | 162.9167 | 165.8333 | 168.3333 | 170.4167 | 172.5 | 174.5833 | 176.6667 | 178.3333 | 180 | 181.6667 | 182.9167 | 184.5833 | 187.0833 | 189.5833 | 191.6667 | 193.75 | 195.4167 | 199.5833 | 202.9167 | 205.8333
23.3 | 135.8333 | 135.8333 | 137.9167 | 143.3333 | 147.9167 | 152.0833 | 155.8333 | 159.1667 | 162.0833 | 165 | 167.5 | 169.5833 | 171.6667 | 173.75 | 175.8333 | 177.5 | 179.1667 | 180.8333 | 182.0833 | 183.75 | 186.25 | 188.75 | 190.8333 | 192.9167 | 194.5833 | 198.75 | 202.0833 | 205
23.4 | 135 | 135 | 137.0833 | 142.5 | 147.0833 | 151.25 | 155 | 158.3333 | 161.25 | 164.1667 | 166.6667 | 168.75 | 170.8333 | 172.9167 | 175 | 176.6667 | 178.3333 | 180 | 181.25 | 182.9167 | 185.4167 | 187.9167 | 190 | 192.0833 | 193.75 | 197.9167 | 201.25 | 204.1667
23.5 | 134.5833 | 134.5833 | 136.6667 | 142.0833 | 146.6667 | 150.8333 | 154.5833 | 157.9167 | 160.8333 | 163.75 | 166.25 | 168.3333 | 170.4167 | 172.5 | 174.5833 | 176.25 | 177.9167 | 179.5833 | 180.8333 | 182.5 | 185 | 187.5 | 189.5833 | 191.6667 | 193.3333 | 197.5 | 200.8333 | 203.75
23.6 | 134.1667 | 134.1667 | 136.25 | 141.6667 | 146.25 | 150.4167 | 154.1667 | 157.5 | 160.4167 | 163.3333 | 165.8333 | 167.9167 | 170 | 172.0833 | 174.1667 | 175.8333 | 177.5 | 179.1667 | 180.4167 | 182.0833 | 184.5833 | 187.0833 | 189.1667 | 191.25 | 192.9167 | 197.0833 | 200.4167 | 203.3333
23.7 | 133.3333 | 133.3333 | 135.4167 | 140.8333 | 145.4167 | 149.5833 | 153.3333 | 156.6667 | 159.5833 | 162.5 | 165 | 167.0833 | 169.1667 | 171.25 | 173.3333 | 175 | 176.6667 | 178.3333 | 179.5833 | 181.25 | 183.75 | 186.25 | 188.3333 | 190.4167 | 192.0833 | 196.25 | 199.5833 | 202.5
23.8 | 132.5 | 132.5 | 134.5833 | 140 | 144.5833 | 148.75 | 152.5 | 155.8333 | 158.75 | 161.6667 | 164.1667 | 166.25 | 168.3333 | 170.4167 | 172.5 | 174.1667 | 175.8333 | 177.5 | 178.75 | 180.4167 | 182.9167 | 185.4167 | 187.5 | 189.5833 | 191.25 | 195.4167 | 198.75 | 201.6667
23.9 | 132.0833 | 132.0833 | 134.1667 | 139.5833 | 144.1667 | 148.3333 | 152.0833 | 155.4167 | 158.3333 | 161.25 | 163.75 | 165.8333 | 167.9167 | 170 | 172.0833 | 173.75 | 175.4167 | 177.0833 | 178.3333 | 180 | 182.5 | 185 | 187.0833 | 189.1667 | 190.8333 | 195 | 198.3333 | 201.25
24 | 131.25 | 131.25 | 133.3333 | 138.75 | 143.3333 | 147.5 | 151.25 | 154.5833 | 157.5 | 160.4167 | 162.9167 | 165 | 167.0833 | 169.1667 | 171.25 | 172.9167 | 174.5833 | 176.25 | 177.5 | 179.1667 | 181.6667 | 184.1667 | 186.25 | 188.3333 | 190 | 194.1667 | 197.5 | 200.4167
24.1 | 130.4167 | 130.4167 | 132.5 | 137.9167 | 142.5 | 146.6667 | 150.4167 | 153.75 | 156.6667 | 159.5833 | 162.0833 | 164.1667 | 166.25 | 168.3333 | 170.4167 | 172.0833 | 173.75 | 175.4167 | 176.6667 | 178.3333 | 180.8333 | 183.3333 | 185.4167 | 187.5 | 189.1667 | 193.3333 | 196.6667 | 199.5833
24.2 | 130 | 130 | 132.0833 | 137.5 | 142.0833 | 146.25 | 150 | 153.3333 | 156.25 | 159.1667 | 161.6667 | 163.75 | 165.8333 | 167.9167 | 170 | 171.6667 | 173.3333 | 175 | 176.25 | 177.9167 | 180.4167 | 182.9167 | 185 | 187.0833 | 188.75 | 192.9167 | 196.25 | 199.1667
24.3 | 129.5833 | 129.5833 | 131.6667 | 137.0833 | 141.6667 | 145.8333 | 149.5833 | 152.9167 | 155.8333 | 158.75 | 161.25 | 163.3333 | 165.4167 | 167.5 | 169.5833 | 171.25 | 172.9167 | 174.5833 | 175.8333 | 177.5 | 180 | 182.5 | 184.5833 | 186.6667 | 188.3333 | 192.5 | 195.8333 | 198.75
24.4 | 128.75 | 128.75 | 130.8333 | 136.25 | 140.8333 | 145 | 148.75 | 152.0833 | 155 | 157.9167 | 160.4167 | 162.5 | 164.5833 | 166.6667 | 168.75 | 170.4167 | 172.0833 | 173.75 | 175 | 176.6667 | 179.1667 | 181.6667 | 183.75 | 185.8333 | 187.5 | 191.6667 | 195 | 197.9167
24.5 | 127.9167 | 127.9167 | 130 | 135.4167 | 140 | 144.1667 | 147.9167 | 151.25 | 154.1667 | 157.0833 | 159.5833 | 161.6667 | 163.75 | 165.8333 | 167.9167 | 169.5833 | 171.25 | 172.9167 | 174.1667 | 175.8333 | 178.3333 | 180.8333 | 182.9167 | 185 | 186.6667 | 190.8333 | 194.1667 | 197.0833
25 | 124.5833 | 124.5833 | 126.6667 | 132.0833 | 136.6667 | 140.8333 | 144.375 | 147.9167 | 159.1667 | 153.5417 | 155.8333 | 158.125 | 160.2083 | 162.0833 | 164.1667 | 165.8333 | 167.5 | 169.1667 | 170.4167 | 172.0833 | 174.5833 | 177.0833 | 178.9583 | 181.25 | 182.7083 | 186.875 | 190.2083 | 193.125
25.1 | 122.5 | 122.5 | 128.75 | 134.1667 | 138.75 | 142.9167 | 146.6667 | 150 | 152.9167 | 155.8333 | 158.3333 | 160.4167 | 162.5 | 164.5833 | 166.6667 | 168.3333 | 170 | 171.6667 | 172.9167 | 174.5833 | 177.0833 | 179.1667 | 181.6667 | 183.3333 | 185.4167 | 189.1667 | 192.5 | 195.4167
25.2 | 122.0833 | 122.0833 | 128.3333 | 133.75 | 138.3333 | 142.0833 | 145.8333 | 149.1667 | 152.0833 | 155 | 157.5 | 159.5833 | 161.6667 | 163.75 | 165.8333 | 167.5 | 169.1667 | 170.4167 | 172.0833 | 173.3333 | 176.25 | 178.3333 | 180.4167 | 182.5 | 184.1667 | 188.3333 | 191.6667 | 194.5833
25.3 | 121.25 | 121.25 | 127.5 | 132.9167 | 137.5 | 141.6667 | 145 | 148.3333 | 151.25 | 154.1667 | 156.6667 | 158.75 | 160.8333 | 162.9167 | 164.5833 | 166.6667 | 168.3333 | 169.5833 | 171.25 | 172.5 | 175 | 177.5 | 179.5833 | 181.6667 | 184.5833 | 187.5 | 190.8333 | 193.75
25.4 | 120.8333 | 120.8333 | 127.0833 | 132.0833 | 136.6667 | 140.8333 | 144.1667 | 147.5 | 150.4167 | 153.3333 | 155.8333 | 157.9167 | 160 | 161.6667 | 163.75 | 165.8333 | 167.0833 | 168.75 | 170.4167 | 171.6667 | 174.1667 | 176.6667 | 178.75 | 180.4167 | 182.5 | 186.25 | 189.5833 | 192.5
25.5 | 120 | 120 | 126.25 | 131.25 | 135.8333 | 140 | 143.75 | 146.6667 | 149.5833 | 152.5 | 155 | 157.0833 | 159.1667 | 161.25 | 162.9167 | 164.5833 | 166.25 | 167.9167 | 169.1667 | 170.8333 | 173.3333 | 175.4167 | 177.5 | 179.5833 | 181.25 | 185.4167 | 188.75 | 191.6667
25.6 | 119.5833 | 119.5833 | 125.4167 | 130.8333 | 135.4167 | 139.1667 | 142.9167 | 145.8333 | 148.75 | 151.6667 | 154.1667 | 156.25 | 158.3333 | 160.4167 | 162.0833 | 163.75 | 165.4167 | 167.0833 | 168.3333 | 170 | 172.5 | 174.5833 | 176.6667 | 178.75 | 180.4167 | 184.1667 | 187.5 | 190.4167
25.7 | 118.75 | 118.75 | 125 | 130 | 134.5833 | 138.3333 | 142.0833 | 145 | 147.9167 | 150.8333 | 153.3333 | 155.4167 | 157.5 | 159.5833 | 161.25 | 162.9167 | 164.5833 | 166.25 | 167.5 | 168.75 | 171.25 | 173.75 | 175.8333 | 177.5 | 179.5833 | 183.3333 | 186.6667 | 189.5833
25.8 | 117.9167 | 117.9167 | 124.1667 | 129.1667 | 133.75 | 137.5 | 141.25 | 144.5833 | 147.0833 | 150 | 152.5 | 154.5833 | 156.6667 | 158.75 | 160.4167 | 162.0833 | 163.75 | 165 | 166.6667 | 167.9167 | 170.4167 | 172.9167 | 174.5833 | 176.6667 | 178.3333 | 182.5 | 185.4167 | 188.3333
25.9 | 117.5 | 117.5 | 123.3333 | 128.3333 | 132.9167 | 137.0833 | 140.4167 | 143.75 | 146.25 | 149.1667 | 151.6667 | 153.75 | 155.8333 | 157.5 | 159.5833 | 161.25 | 162.9167 | 164.1667 | 165.8333 | 167.0833 | 169.5833 | 171.6667 | 173.75 | 175.8333 | 177.5 | 181.25 | 184.5833 | 187.5
26 | 116.6667 | 116.6667 | 122.5 | 127.9167 | 132.0833 | 136.25 | 139.5833 | 142.9167 | 145.4167 | 148.3333 | 150.4167 | 152.9167 | 155 | 156.6667 | 158.75 | 160.4167 | 161.6667 | 163.3333 | 164.5833 | 166.25 | 168.3333 | 170.8333 | 172.9167 | 174.5833 | 176.6667 | 180.4167 | 183.3333 | 186.25
26.1 | 115.8333 | 115.8333 | 122.0833 | 127.0833 | 131.6667 | 135.4167 | 138.75 | 142.0833 | 145 | 147.5 | 149.5833 | 152.0833 | 154.1667 | 155.8333 | 157.5 | 159.1667 | 160.8333 | 162.5 | 163.75 | 165 | 167.5 | 170 | 171.6667 | 173.75 | 175.4167 | 179.1667 | 182.5 | 185.4167
26.2 | 115.4167 | 115.4167 | 120.8333 | 126.25 | 130.8333 | 134.5833 | 137.9167 | 141.25 | 144.1667 | 146.6667 | 148.75 | 151.25 | 152.9167 | 155 | 156.6667 | 158.3333 | 160 | 161.6667 | 162.9167 | 164.1667 | 166.6667 | 168.75 | 170.8333 | 172.9167 | 174.5833 | 178.3333 | 181.25 | 184.1667
26.3 | 114.5833 | 114.5833 | 120.4167 | 125.4167 | 130 | 133.75 | 137.0833 | 140.4167 | 142.9167 | 145.8333 | 147.9167 | 150.4167 | 152.0833 | 154.1667 | 155.8333 | 157.5 | 159.1667 | 160.4167 | 162.0833 | 163.3333 | 165.8333 | 167.9167 | 170 | 171.6667 | 173.3333 | 177.0833 | 180.4167 | 183.3333
26.4 | 114.1667 | 114.1667 | 120 | 125 | 129.1667 | 132.9167 | 136.25 | 138.75 | 142.0833 | 145 | 147.0833 | 149.1667 | 151.25 | 153.3333 | 155 | 157.5 | 158.3333 | 159.5833 | 160.8333 | 162.0833 | 164.5833 | 167.0833 | 168.75 | 170.8333 | 172.5 | 176.25 | 179.1667 | 182.0833
26.5 | 113.3333 | 113.3333 | 119.1667 | 124.1667 | 127.5 | 132.0833 | 135.4167 | 138.75 | 141.25 | 144.1667 | 146.25 | 148.3333 | 150.4167 | 152.5 | 154.1667 | 155.8333 | 157.0833 | 158.75 | 160 | 161.25 | 163.75 | 165.8333 | 167.9167 | 169.5833 | 171.25 | 175 | 178.3333 | 180.8333
26.6 | 112.5 | 112.5 | 118.3333 | 123.3333 | 127.5 | 131.25 | 135 | 137.5 | 140.4167 | 142.9167 | 145.4167 | 147.5 | 149.5833 | 151.25 | 153.3333 | 154.5833 | 156.25 | 157.9167 | 159.1667 | 160.4167 | 162.9167 | 165 | 167.0833 | 168.75 | 170.4167 | 174.1667 | 177.0833 | 180
26.7 | 112.0833 | 112.0833 | 117.9167 | 122.5 | 127.0833 | 130.8333 | 134.1667 | 137.0833 | 139.5833 | 142.0833 | 144.5833 | 146.6667 | 148.75 | 150.4167 | 152.5 | 153.75 | 155.4167 | 157.5 | 157.9167 | 159.5833 | 161.6667 | 163.75 | 165.8333 | 167.9167 | 169.5833 | 172.9167 | 176.25 | 178.75
26.8 | 111.25 | 111.25 | 117.0833 | 121.6667 | 126.25 | 130 | 133.3333 | 136.25 | 138.75 | 141.25 | 143.75 | 145.8333 | 147.9167 | 149.5833 | 151.25 | 152.9167 | 154.5833 | 155.8333 | 157.0833 | 158.3333 | 160.8333 | 162.9167 | 165 | 166.6667 | 168.3333 | 172.0833 | 175 | 177.9167
26.9 | 110.4167 | 110.4167 | 115.8333 | 121.25 | 125.4167 | 129.1667 | 132.5 | 135.4167 | 137.9167 | 140.4167 | 142.9167 | 145 | 146.6667 | 148.75 | 150.4167 | 152.0833 | 153.3333 | 155 | 156.25 | 157.5 | 160 | 162.0833 | 163.75 | 165.8333 | 167.5 | 170.8333 | 174.1667 | 176.6667
27 | 110 | 110 | 115.4167 | 120.4167 | 124.5833 | 128.3333 | 131.6667 | 134.5833 | 137.0833 | 139.5833 | 142.0833 | 144.1667 | 145.8333 | 147.9167 | 149.5833 | 150.8333 | 153.3333 | 153.75 | 155.4167 | 156.6667 | 158.75 | 160.8333 | 162.9167 | 164.5833 | 166.25 | 170 | 172.9167 | 175.4167
27.1 | 109.1667 | 109.1667 | 115 | 119.5833 | 123.75 | 127.5 | 130.8333 | 133.75 | 136.25 | 138.75 | 140.8333 | 142.9167 | 144.1667 | 146.6667 | 148.3333 | 150 | 151.6667 | 152.9167 | 154.1667 | 155.4167 | 157.9167 | 160 | 161.6667 | 163.75 | 165.4167 | 168.75 | 172.0833 | 174.5833
27.2 | 108.3333 | 108.3333 | 114.1667 | 118.75 | 122.9167 | 126.6667 | 130 | 132.9167 | 135.4167 | 137.9167 | 140.8333 | 142.0833 | 144.1667 | 145.8333 | 147.5 | 149.1667 | 150.4167 | 152.0833 | 153.3333 | 154.5833 | 156.6667 | 158.75 | 160.8333 | 162.5 | 165 | 167.9167 | 170.8333 | 173.3333
27.3 | 107.9167 | 107.9167 | 113.3333 | 117.9167 | 122.5 | 125.8333 | 129.1667 | 132.0833 | 134.5833 | 137.0833 | 139.1667 | 141.25 | 143.3333 | 145 | 146.6667 | 148.3333 | 149.5833 | 150.8333 | 152.5 | 153.3333 | 155.8333 | 157.9167 | 160 | 161.6667 | 163.3333 | 166.6667 | 169.5833 | 172.0833
27.4 | 107.0833 | 107.0833 | 112.5 | 117.5 | 121.25 | 125 | 128.3333 | 131.25 | 133.75 | 136.25 | 138.3333 | 140.4167 | 142.0833 | 144.1667 | 145.8333 | 147.0833 | 148.75 | 150 | 151.25 | 152.5 | 155 | 157.0833 | 158.75 | 160.4167 | 162.0833 | 165.8333 | 168.75 | 171.25
27.5 | 106.25 | 106.25 | 111.6667 | 116.6667 | 120.4167 | 124.1667 | 127.5 | 130.4167 | 132.9167 | 135.4167 | 137.5 | 139.5833 | 141.25 | 142.9167 | 144.5833 | 146.25 | 147.5 | 149.1667 | 150.4167 | 151.6667 | 153.75 | 155.8333 | 157.9167 | 159.5833 | 161.25 | 164.5833 | 167.5 | 170
27.6 | 105.8333 | 105.8333 | 111.25 | 115.8333 | 119.5833 | 123.3333 | 126.6667 | 129.1667 | 132.0833 | 134.1667 | 136.6667 | 138.3333 | 140.4167 | 142.0833 | 143.75 | 145.4167 | 146.6667 | 147.9167 | 149.1667 | 150.4167 | 152.9167 | 155 | 156.6667 | 158.3333 | 160 | 163.3333 | 166.25 | 168.75
27.7 | 105 | 105 | 110.4167 | 115 | 119.1667 | 122.5 | 125.8333 | 128.3333 | 131.25 | 133.3333 | 135.4167 | 137.5 | 139.5833 | 141.25 | 142.9167 | 144.1667 | 145.8333 | 147.0833 | 148.3333 | 149.5833 | 151.6667 | 153.75 | 155.8333 | 157.5 | 158.75 | 162.5 | 165.4167 | 167.9167
27.8 | 104.1667 | 104.1667 | 109.5833 | 114.1667 | 118.3333 | 121.6667 | 125 | 127.5 | 130 | 132.5 | 134.5833 | 136.6667 | 138.3333 | 140.4167 | 141.6667 | 143.3333 | 144.5833 | 146.25 | 147.5 | 148.75 | 150.8333 | 152.9167 | 154.5833 | 156.25 | 157.9167 | 161.25 | 164.1667 | 166.6667
27.9 | 103.3333 | 103.3333 | 108.75 | 113.3333 | 117.5 | 120.8333 | 124.1667 | 126.6667 | 129.1667 | 131.6667 | 133.75 | 135.8333 | 137.5 | 139.1667 | 140.8333 | 142.5 | 143.75 | 145 | 146.25 | 147.5 | 149.5833 | 151.6667 | 153.75 | 155.4167 | 156.6667 | 160.4167 | 162.9167 | 165.4167
28 | 102.9167 | 102.9167 | 107.9167 | 112.5 | 116.6667 | 120 | 122.9167 | 125.8333 | 128.3333 | 130.8333 | 132.9167 | 135 | 136.6667 | 138.3333 | 140 | 141.25 | 142.9167 | 144.1667 | 145.4167 | 146.6667 | 148.75 | 150.8333 | 152.5 | 154.1667 | 155.8333 | 159.1667 | 162.0833 | 164.5833
28.1 | 102.0833 | 102.0833 | 107.5 | 111.6667 | 115.8333 | 119.1667 | 122.0833 | 125 | 127.5 | 130 | 132.0833 | 133.75 | 135.8333 | 137.5 | 138.75 | 140.4167 | 141.6667 | 142.9167 | 144.1667 | 145.4167 | 147.5 | 149.5833 | 151.6667 | 152.9167 | 154.5833 | 157.9167 | 160.8333 | 163.3333
28.2 | 101.25 | 101.25 | 106.6667 | 110.8333 | 115 | 118.3333 | 121.25 | 124.1667 | 126.6667 | 128.75 | 130.8333 | 132.9167 | 134.5833 | 136.25 | 137.9167 | 139.5833 | 140.8333 | 142.0833 | 143.3333 | 144.5833 | 146.6667 | 148.75 | 150.4167 | 152.0833 | 153.75 | 157.0833 | 159.5833 | 162.0833
28.3 | 100.4167 | 100.4167 | 105.8333 | 110.8333 | 114.1667 | 117.5 | 120.4167 | 123.3333 | 125.8333 | 127.9167 | 130 | 132.0833 | 133.75 | 135.4167 | 137.0833 | 138.3333 | 140 | 141.25 | 142.5 | 143.3333 | 145.4167 | 147.5 | 149.1667 | 150.8333 | 152.5 | 155.8333 | 158.75 | 160.8333
28.4 | 100 | 100 | 105 | 109.5833 | 113.3333 | 116.6667 | 119.5833 | 122.5 | 125 | 127.0833 | 129.1667 | 130.8333 | 132.9167 | 134.5833 | 135.8333 | 137.5 | 138.75 | 140 | 141.25 | 142.5 | 144.5833 | 146.6667 | 148.3333 | 150 | 151.25 | 154.5833 | 157.5 | 160
28.5 | 99.1667 | 99.1667 | 104.1667 | 108.75 | 112.5 | 115.8333 | 118.75 | 121.6667 | 123.75 | 126.25 | 128.3333 | 130 | 131.6667 | 133.3333 | 135 | 136.25 | 137.9167 | 139.1667 | 140.4167 | 141.25 | 143.3333 | 145.4167 | 147.0833 | 148.75 | 150.4167 | 153.75 | 156.25 | 158.75
28.6 | 97.9167 | 97.9167 | 103.3333 | 107.9167 | 111.6667 | 115 | 117.9167 | 120.4167 | 122.9167 | 125 | 127.0833 | 129.1667 | 130.8333 | 131.6667 | 134.1667 | 135.4167 | 136.6667 | 137.9167 | 139.1667 | 140.4167 | 142.5 | 144.1667 | 146.25 | 147.5 | 149.1667 | 152.5 | 155 | 157.5
28.7 | 97.0833 | 97.0833 | 102.9167 | 107.0833 | 110.8333 | 114.1667 | 117.0833 | 119.5833 | 122.0833 | 124.1667 | 126.25 | 128.3333 | 130 | 131.6667 | 132.9167 | 134.5833 | 135.8333 | 137.0833 | 138.3333 | 139.1667 | 141.25 | 143.3333 | 145 | 146.6667 | 147.9167 | 151.25 | 154.1667 | 156.25
28.8 | 95.8333 | 95.8333 | 102.0833 | 106.25 | 110 | 113.3333 | 116.25 | 118.75 | 121.25 | 123.3333 | 125.4167 | 127.0833 | 128.75 | 130.4167 | 132.0833 | 133.3333 | 134.5833 | 135.8333 | 137.0833 | 138.3333 | 140.4167 | 142.0833 | 143.75 | 145.4167 | 147.0833 | 150 | 152.9167 | 155
28.9 | 94.5833 | 94.5833 | 101.25 | 105.4167 | 109.1667 | 112.5 | 115.4167 | 117.9167 | 120.4167 | 122.5 | 124.5833 | 126.25 | 127.9167 | 129.5833 | 130.8333 | 132.5 | 133.75 | 135 | 136.25 | 137.0833 | 139.1667 | 141.25 | 142.9167 | 144.5833 | 145.8333 | 149.1667 | 151.6667 | 154.1667
29 | 93.75 | 93.75 | 100.4167 | 104.5833 | 109.1667 | 111.6667 | 114.1667 | 117.0833 | 119.1667 | 121.25 | 123.3333 | 125.4167 | 127.0833 | 128.3333 | 130 | 131.25 | 132.5 | 133.75 | 135 | 136.25 | 138.3333 | 140 | 141.6667 | 143.3333 | 144.5833 | 147.9167 | 150.4167 | 152.9167
29.1 | 92.5 | 92.5 | 100 | 103.75 | 107.5 | 110.4167 | 113.3333 | 115.8333 | 118.3333 | 120.4167 | 122.5 | 124.1667 | 125.8333 | 127.5 | 129.1667 | 130.4167 | 132.5 | 132.9167 | 134.1667 | 135 | 137.0833 | 139.1667 | 140.8333 | 142.0833 | 143.75 | 146.6667 | 149.1667 | 151.6667
29.2 | 91.6667 | 91.6667 | 98.75 | 102.9167 | 106.6667 | 109.5833 | 112.5 | 115 | 117.5 | 119.5833 | 121.6667 | 123.3333 | 125 | 126.6667 | 127.9167 | 129.1667 | 130.4167 | 131.6667 | 132.9167 | 134.1667 | 136.25 | 137.9167 | 139.5833 | 141.25 | 142.5 | 145.4167 | 148.3333 | 150.4167
29.3 | 90.4167 | 90.4167 | 97.5 | 102.0833 | 105.8333 | 108.75 | 111.6667 | 114.1667 | 116.6667 | 118.75 | 120.4167 | 122.5 | 124.1667 | 125.4167 | 127.0833 | 128.3333 | 129.5833 | 130.8333 | 132.0833 | 132.9167 | 135 | 136.6667 | 138.3333 | 140 | 141.25 | 144.5833 | 147.0833 | 149.1667
29.4 | 89.1667 | 89.1667 | 96.25 | 101.25 | 105 | 107.9167 | 110.8333 | 113.3333 | 115.4167 | 117.5 | 119.5833 | 121.25 | 122.9167 | 124.5833 | 125.8333 | 127.0833 | 128.3333 | 129.5833 | 130.8333 | 132.0833 | 133.75 | 135.8333 | 137.5 | 138.75 | 140 | 143.3333 | 145.8333 | 147.9167
29.5 | 87.9167 | 87.9167 | 95 | 100.4167 | 104.1667 | 107.0833 | 110 | 112.5 | 114.5833 | 116.6667 | 118.75 | 120.4167 | 122.0833 | 123.3333 | 125 | 126.25 | 127.5 | 128.75 | 129.5833 | 130.8333 | 132.9167 | 134.5833 | 136.25 | 137.5 | 139.1667 | 142.0833 | 143.75 | 146.6667
29.6 | 87.0833 | 87.0833 | 93.75 | 100 | 102.9167 | 106.25 | 108.75 | 111.25 | 113.75 | 115.8333 | 117.5 | 119.1667 | 120.8333 | 122.5 | 123.75 | 125 | 126.25 | 127.5 | 128.75 | 129.5833 | 131.6667 | 133.3333 | 135 | 136.6667 | 137.9167 | 140.8333 | 142.0833 | 145.8333
29.7 | 85.8333 | 85.8333 | 92.5 | 98.75 | 102.0833 | 105.4167 | 107.9167 | 110.4167 | 112.9167 | 114.5833 | 116.6667 | 118.3333 | 120 | 121.25 | 122.9167 | 124.1667 | 125.4167 | 126.6667 | 127.0833 | 128.75 | 130.4167 | 132.5 | 133.75 | 135.4167 | 136.6667 | 139.5833 | 141.6667 | 144.5833
29.8 | 84.5833 | 84.5833 | 91.25 | 97.5 | 101.25 | 104.5833 | 107.0833 | 109.5833 | 111.6667 | 113.75 | 115.4167 | 117.5 | 118.75 | 120.4167 | 121.6667 | 122.9167 | 124.1667 | 125.4167 | 126.6667 | 127.5 | 129.5833 | 131.25 | 132.9167 | 134.1667 | 135.4167 | 138.75 | 141.25 | 143.3333
29.9 | 83.75 | 83.75 | 90 | 95.8333 | 100.4167 | 103.3333 | 106.25 | 108.75 | 110.8333 | 112.9167 | 114.5833 | 116.25 | 117.9167 | 119.1667 | 120.8333 | 122.0833 | 123.3333 | 124.5833 | 125.4167 | 126.6667 | 128.3333 | 130 | 131.6667 | 132.9167 | 134.5833 | 137.5 | 140 | 142.0833
30 | 82.5 | 82.5 | 88.75 | 94.5833 | 100 | 102.5 | 105.4167 | 107.5 | 110 | 111.6667 | 113.75 | 115.4167 | 117.0833 | 118.3333 | 119.5833 | 120.8333 | 122.0833 | 123.3333 | 124.1667 | 125.4167 | 127.0833 | 129.1667 | 130.4167 | 132.0833 | 133.3333 | 136.25 | 138.75 | 140.8333
30.1 | 81.25 | 81.25 | 87.5 | 93.3333 | 98.75 | 101.6667 | 104.1667 | 106.6667 | 108.75 | 110.8333 | 112.5 | 114.1667 | 115.8333 | 117.5 | 118.75 | 120 | 121.25 | 122.0833 | 123.3333 | 124.1667 | 126.25 | 127.9167 | 129.5833 | 130.8333 | 132.0833 | 135 | 137.5 | 139.5833
30.2 | 80 | 80 | 86.25 | 92.0833 | 97.0833 | 100.8333 | 103.3333 | 105.8333 | 107.9167 | 110 | 111.6667 | 113.3333 | 115 | 116.25 | 117.5 | 118.75 | 120 | 121.25 | 122.0833 | 123.3333 | 125 | 126.6667 | 128.3333 | 129.5833 | 130.8333 | 133.75 | 136.25 | 138.3333
30.3 | 78.75 | 78.75 | 85 | 90.8333 | 95.8333 | 100 | 102.5 | 105 | 107.0833 | 108.75 | 110.4167 | 112.0833 | 113.75 | 115 | 116.6667 | 117.9167 | 118.75 | 120 | 121.25 | 122.0833 | 123.75 | 125.4167 | 127.0833 | 128.3333 | 129.5833 | 132.5 | 135 | 137.0833
30.4 | 77.9167 | 77.9167 | 83.75 | 89.5833 | 95 | 98.75 | 101.6667 | 103.75 | 105.8333 | 107.9167 | 109.5833 | 111.25 | 112.9167 | 114.1667 | 115.4167 | 116.6667 | 117.9167 | 118.75 | 120 | 120.8333 | 122.9167 | 124.5833 | 125.8333 | 127.5 | 128.75 | 131.25 | 133.75 | 135.8333
30.5 | 76.6667 | 76.6667 | 81.6667 | 87.9167 | 92.9167 | 97.5 | 100.4167 | 102.9167 | 105 | 106.6667 | 108.75 | 110 | 111.6667 | 112.9167 | 114.5833 | 115.4167 | 116.6667 | 117.9167 | 118.75 | 120 | 121.6667 | 123.3333 | 124.5833 | 126.25 | 127.5 | 130 | 132.5 | 134.5833
30.6 | 75.4167 | 75.4167 | 81.25 | 86.6667 | 91.6667 | 95.8333 | 100 | 102.0833 | 103.75 | 105.8333 | 107.5 | 109.1667 | 110.8333 | 112.0833 | 113.3333 | 114.5833 | 115.8333 | 116.6667 | 117.9167 | 118.75 | 120.4167 | 122.0833 | 123.75 | 125 | 126.25 | 128.75 | 131.25 | 133.3333
30.7 | 74.1667 | 74.1667 | 80 | 85.4167 | 90 | 94.5833 | 98.3333 | 100.8333 | 102.9167 | 105 | 106.6667 | 107.9167 | 109.5833 | 110.8333 | 112.0833 | 113.3333 | 114.5833 | 115.4167 | 116.6667 | 117.5 | 119.1667 | 120.8333 | 122.5 | 123.75 | 125 | 127.9167 | 130 | 132.5
30.8 | 72.9167 | 72.9167 | 78.75 | 84.1667 | 88.75 | 92.9167 | 97.0833 | 100 | 102.0833 | 103.75 | 105.4167 | 107.0833 | 108.3333 | 110 | 111.25 | 112.5 | 113.3333 | 114.5833 | 115.4167 | 116.25 | 118.3333 | 119.5833 | 121.25 | 122.5 | 123.75 | 126.6667 | 128.3333 | 130.8333
30.9 | 71.6667 | 71.6667 | 77.5 | 82.5 | 87.0833 | 91.6667 | 95.4167 | 98.75 | 100.8333 | 102.9167 | 104.5833 | 105.8333 | 107.5 | 108.75 | 110 | 111.25 | 112.5 | 113.3333 | 114.1667 | 115.4167 | 117.0833 | 118.75 | 120 | 121.25 | 122.5 | 125.4167 | 127.5 | 129.1667
31 | 70.8333 | 70.8333 | 76.25 | 81.25 | 85.8333 | 90 | 93.75 | 97.0833 | 100 | 101.6667 | 103.3333 | 105 | 106.25 | 107.9167 | 109.1667 | 110 | 111.25 | 112.0833 | 113.3333 | 114.1667 | 115.8333 | 117.5 | 118.75 | 120.8333 | 121.25 | 124.1667 | 126.25 | 128.3333
31.1 | 69.5833 | 69.5833 | 75 | 80 | 84.5833 | 88.3333 | 92.0833 | 95.8333 | 98.75 | 100.8333 | 102.5 | 103.75 | 105.4167 | 106.6667 | 107.9167 | 109.1667 | 110 | 111.25 | 112.0833 | 112.9167 | 114.5833 | 116.25 | 117.5 | 118.75 | 120 | 122.9167 | 125 | 127.0833
31.2 | 68.3333 | 68.3333 | 73.75 | 78.75 | 82.9167 | 87.0833 | 90.4167 | 94.1667 | 97.0833 | 99.5833 | 101.25 | 102.9167 | 104.1667 | 105.4167 | 106.6667 | 107.9167 | 109.1667 | 110 | 110.8333 | 111.6667 | 113.75 | 115 | 116.6667 | 117.9167 | 118.75 | 121.6667 | 123.75 | 125.4167
31.3 | 67.0833 | 67.0833 | 72.5 | 77.0833 | 81.6667 | 85.4167 | 89.1667 | 92.5 | 95.4167 | 99.1667 | 100.4167 | 101.6667 | 103.3333 | 104.5833 | 105.8333 | 106.6667 | 107.9167 | 108.75 | 110 | 110.8333 | 112.5 | 113.75 | 115.4167 | 116.6667 | 117.5 | 120.4167 | 122.5 | 124.1667
31.4 | 65.8333 | 65.8333 | 71.25 | 75.8333 | 80 | 83.75 | 87.5 | 90.8333 | 93.75 | 96.6667 | 99.1667 | 100.8333 | 102.0833 | 103.3333 | 104.5833 | 105.8333 | 106.6667 | 107.9167 | 108.75 | 109.5833 | 111.25 | 112.5 | 114.1667 | 115.4167 | 116.6667 | 119.1667 | 121.25 | 122.9167
31.5 | 64.5833 | 64.5833 | 69.5833 | 74.5833 | 78.75 | 81.6667 | 85.8333 | 89.1667 | 92.0833 | 95 | 97.5 | 99.5833 | 100.8333 | 102.0833 | 103.3333 | 104.5833 | 105.4167 | 106.6667 | 107.5 | 108.3333 | 110 | 111.6667 | 112.9167 | 114.1667 | 115.4167 | 117.9167 | 120 | 121.6667
31.6 | 63.3333 | 63.3333 | 68.3333 | 72.9167 | 77.0833 | 80.8333 | 84.1667 | 87.5 | 90.4167 | 93.3333 | 95.8333 | 98.3333 | 100 | 101.25 | 102.5 | 103.3333 | 104.5833 | 105.4167 | 106.25 | 107.0833 | 108.75 | 110.4167 | 111.6667 | 112.9167 | 114.1667 | 116.6667 | 118.75 | 120.4167
31.7 | 62.0833 | 62.0833 | 67.0833 | 71.6667 | 75.4167 | 79.1667 | 82.5 | 85.8333 | 88.75 | 91.25 | 93.75 | 96.25 | 98.75 | 100 | 101.25 | 102.0833 | 102.5 | 104.1667 | 105 | 105.8333 | 107.5 | 109.1667 | 110.4167 | 111.6667 | 112.9167 | 115 | 117.0833 | 118.75
31.8 | 60.8333 | 60.8333 | 65.8333 | 70 | 74.1667 | 77.9167 | 80.8333 | 84.1667 | 87.0833 | 89.5833 | 92.0833 | 94.5833 | 96.6667 | 98.75 | 100 | 101.25 | 102.0833 | 102.9167 | 104.1667 | 105 | 106.25 | 107.9167 | 109.1667 | 110.4167 | 111.6667 | 113.75 | 115.8333 | 117.9167
31.9 | 59.5833 | 59.5833 | 64.5833 | 68.75 | 72.5 | 76.25 | 79.5833 | 82.5 | 85 | 87.9167 | 90.4167 | 92.5 | 94.5833 | 96.6667 | 98.75 | 100 | 100.8333 | 102.0833 | 102.9167 | 103.75 | 105.4167 | 106.6667 | 107.9167 | 109.1667 | 110.4167 | 112.9167 | 114.5833 | 116.25
32 | 58.3333 | 58.3333 | 63.3333 | 67.5 | 71.25 | 74.5833 | 77.9167 | 80.8333 | 83.3333 | 85.8333 | 88.3333 | 90.8333 | 92.9167 | 95 | 96.6667 | 98.75 | 100 | 100.8333 | 101.6667 | 102.5 | 104.1667 | 105.4167 | 106.6667 | 107.9167 | 108.75 | 111.25 | 113.3333 | 115
32.1 | 57.0833 | 57.0833 | 61.6667 | 65.8333 | 69.5833 | 72.9167 | 76.25 | 79.1667 | 81.6667 | 84.1667 | 86.6667 | 88.75 | 90.8333 | 92.9167 | 95 | 96.6667 | 98.3333 | 99.5833 | 100.4167 | 101.25 | 102.9167 | 104.1667 | 105.4167 | 106.6667 | 107.5 | 110 | 112.0833 | 113.75
32.2 | 55.8333 | 55.8333 | 60.4167 | 64.5833 | 67.9167 | 71.25 | 74.5833 | 77.5 | 80 | 82.5 | 84.5833 | 87.0833 | 89.1667 | 90.8333 | 92.9167 | 94.5833 | 96.25 | 97.9167 | 99.5833 | 100 | 101.6667 | 102.9167 | 104.1667 | 105.4167 | 106.25 | 108.75 | 110.8333 | 112.5
32.3 | 54.5833 | 54.5833 | 59.1667 | 62.9167 | 66.6667 | 70 | 72.9167 | 75.4167 | 78.3333 | 80.4167 | 81.6667 | 85 | 87.0833 | 88.75 | 90.8333 | 92.5 | 94.1667 | 95.8333 | 97.0833 | 98.75 | 100.4167 | 101.6667 | 102.9167 | 104.1667 | 105 | 107.5 | 109.1667 | 111.25
32.4 | 53.3333 | 53.75 | 57.9167 | 61.6667 | 65.8333 | 68.3333 | 71.25 | 73.75 | 76.25 | 78.75 | 80.8333 | 82.9167 | 85 | 87.0833 | 88.75 | 90.4167 | 92.0833 | 93.75 | 95 | 96.6667 | 99.1667 | 100.4167 | 101.6667 | 102.9167 | 103.75 | 106.25 | 107.9167 | 109.5833
32.5 | 52.0833 | 52.0833 | 56.25 | 60 | 63.75 | 66.6667 | 69.5833 | 72.0833 | 74.5833 | 77.0833 | 79.1667 | 81.25 | 82.9167 | 85 | 86.6667 | 88.3333 | 90 | 91.25 | 92.9167 | 95 | 97.0833 | 99.1667 | 100.4167 | 101.6667 | 102.5 | 105 | 107.5 | 108.3333
32.6 | 50.8333 | 50.8333 | 55 | 58.75 | 62.0833 | 65 | 67.9167 | 70.4167 | 72.9167 | 75 | 77.0833 | 79.1667 | 81.25 | 82.9167 | 84.5833 | 86.25 | 87.9167 | 89.1667 | 90.8333 | 92.0833 | 94.5833 | 97.0833 | 99.1667 | 100.4167 | 101.25 | 103.3333 | 105.4167 | 107.0833
32.7 | 49.5833 | 49.5833 | 53.75 | 57.0833 | 60.4167 | 63.3333 | 66.25 | 68.3333 | 70.8333 | 73.3333 | 75.4167 | 77.0833 | 79.1667 | 80.8333 | 82.5 | 84.1667 | 85.4167 | 87.0833 | 88.3333 | 90 | 92.5 | 94.5833 | 96.6667 | 98.75 | 100 | 102.0833 | 104.1667 | 105.4167
32.8 | 48.3333 | 48.3333 | 52.0833 | 55.8333 | 58.75 | 61.6667 | 64.5833 | 67.0833 | 69.1667 | 71.25 | 73.3333 | 75.4167 | 77.0833 | 78.75 | 80.4167 | 82.0833 | 83.3333 | 85 | 86.25 | 87.5 | 90 | 92.0833 | 94.5833 | 96.25 | 98.3333 | 100.8333 | 102.5 | 104.1667
32.9 | 47.0833 | 47.0833 | 50.8333 | 54.1667 | 57.5 | 60 | 62.9167 | 65 | 67.5 | 69.5833 | 71.6667 | 73.3333 | 75 | 76.6667 | 78.3333 | 80 | 81.25 | 82.5 | 84.1667 | 85.4167 | 87.5 | 90 | 92.0833 | 93.75 | 99.1667 | 100 | 101.25 | 102.9167
33 | 45.8333 | 45.8333 | 49.5833 | 52.9167 | 55.8333 | 58.3333 | 61.25 | 63.3333 | 65.4167 | 67.5 | 69.5833 | 71.25 | 72.9167 | 74.5833 | 76.25 | 77.9167 | 79.1667 | 80.4167 | 81.6667 | 82.9167 | 85.4167 | 87.5 | 89.5833 | 91.25 | 93.3333 | 97.0833 | 100 | 101.25
33.1 | 44.1667 | 44.1667 | 47.9167 | 51.25 | 54.1667 | 57.0833 | 59.1667 | 61.6667 | 63.75 | 65.8333 | 67.5 | 69.5833 | 71.25 | 72.5 | 74.5833 | 75.4167 | 77.0833 | 78.3333 | 79.5833 | 80.8333 | 82.9167 | 85 | 87.0833 | 88.75 | 91.25 | 94.5833 | 97.9167 | 100
33.2 | 42.9167 | 42.9167 | 46.6667 | 49.5833 | 52.5 | 55.4167 | 57.5 | 60 | 62.0833 | 63.75 | 65.8333 | 67.5 | 69.1667 | 70.4167 | 72.0833 | 73.3333 | 74.5833 | 75.8333 | 77.0833 | 78.3333 | 80.4167 | 81.6667 | 84.5833 | 86.25 | 87.9167 | 92.0833 | 95.4167 | 98.3333
33.3 | 41.6667 | 41.6667 | 45 | 48.3333 | 51.25 | 53.75 | 55.8333 | 57.9167 | 60 | 62.0833 | 63.75 | 65.4167 | 67.0833 | 68.3333 | 70 | 71.25 | 72.5 | 73.75 | 75 | 76.25 | 78.3333 | 80.4167 | 82.0833 | 83.75 | 85.4167 | 89.1667 | 92.5 | 95.4167
33.4 | 40.4167 | 40.4167 | 43.75 | 46.6667 | 49.5833 | 52.0833 | 54.1667 | 56.25 | 58.3333 | 60 | 61.6667 | 63.3333 | 65 | 66.25 | 67.9167 | 69.1667 | 70.4167 | 71.6667 | 72.5 | 73.75 | 75.8333 | 77.9167 | 79.5833 | 81.25 | 82.9167 | 86.6667 | 89.5833 | 92.5
33.5 | 39.1667 | 39.1667 | 42.5 | 45.4167 | 47.9167 | 50.4167 | 53.3333 | 54.5833 | 56.25 | 58.3333 | 60 | 61.25 | 62.9167 | 64.1667 | 65.4167 | 67.0833 | 67.9167 | 69.1667 | 70.4167 | 71.25 | 73.3333 | 75.4167 | 77.0833 | 78.75 | 80.4167 | 83.75 | 86.6667 | 89.5833
33.6 | 37.9167 | 37.9167 | 40.8333 | 43.75 | 46.25 | 48.75 | 50.8333 | 52.5 | 54.5833 | 56.25 | 57.9167 | 59.1667 | 60.8333 | 62.0833 | 63.3333 | 64.5833 | 65.8333 | 67.0833 | 67.9167 | 69.1667 | 71.25 | 72.9167 | 74.5833 | 76.25 | 77.5 | 80.4167 | 84.1667 | 85.8333
33.7 | 36.25 | 36.25 | 39.5833 | 42.0833 | 44.5833 | 47.0833 | 48.75 | 50.8333 | 52.5 | 54.1667 | 56.25 | 57.5 | 58.75 | 60 | 61.25 | 62.5 | 63.75 | 64.5833 | 65.8333 | 66.6667 | 68.75 | 70.4167 | 72.0833 | 73.75 | 75 | 78.3333 | 81.25 | 83.75
33.8 | 35 | 35 | 37.9167 | 40.8333 | 42.9167 | 45 | 47.0833 | 49.1667 | 50.8333 | 53.3333 | 53.75 | 55.4167 | 56.6667 | 57.9167 | 59.1667 | 60.4167 | 61.25 | 62.5 | 63.3333 | 64.5833 | 66.25 | 67.9167 | 69.5833 | 70.8333 | 72.5 | 75.4167 | 78.3333 | 80.8333
33.9 | 33.75 | 33.75 | 36.6667 | 39.1667 | 41.25 | 43.3333 | 45.4167 | 47.0833 | 48.75 | 50.4167 | 51.6667 | 53.3333 | 54.5833 | 55.8333 | 57.0833 | 57.9167 | 59.1667 | 60 | 61.25 | 62.0833 | 63.75 | 65.4167 | 67.0833 | 68.3333 | 69.5833 | 72.0833 | 75.4167 | 77.9167
34 | 32.5 | 32.5 | 35 | 37.5 | 39.5833 | 41.6667 | 43.75 | 45.4167 | 47.0833 | 47.9167 | 50 | 51.25 | 52.5 | 53.75 | 54.5833 | 55.8333 | 56.6667 | 57.9167 | 58.75 | 59.5833 | 61.25 | 62.9167 | 64.5833 | 65.8333 | 67.0833 | 69.1667 | 72.5 | 75
34.1 | 30.8333 | 30.8333 | 33.75 | 35.8333 | 37.9167 | 40 | 41.6667 | 43.3333 | 45.4167 | 46.6667 | 47.9167 | 49.1667 | 50.4167 | 51.25 | 52.5 | 53.75 | 54.5833 | 55.4167 | 56.25 | 57.0833 | 58.75 | 60.4167 | 61.6667 | 63.3333 | 64.5833 | 67.0833 | 69.5833 | 72.0833
34.2 | 29.5833 | 29.5833 | 32.0833 | 34.5833 | 36.6667 | 38.3333 | 40 | 41.6667 | 42.9167 | 44.5833 | 45.8333 | 47.0833 | 49.1667 | 49.1667 | 50.4167 | 51.25 | 52.0833 | 53.3333 | 54.1667 | 55 | 56.25 | 57.9167 | 59.1667 | 60.4167 | 61.6667 | 64.5833 | 66.6667 | 69.1667
34.3 | 28.3333 | 28.3333 | 30.8333 | 32.9167 | 35 | 36.6667 | 38.3333 | 39.5833 | 41.25 | 42.5 | 43.75 | 45 | 45.8333 | 47.0833 | 47.9167 | 49.1667 | 50 | 50.8333 | 51.6667 | 52.5 | 54.1667 | 55.4167 | 56.6667 | 57.9167 | 59.1667 | 60.8333 | 63.75 | 65.8333
34.4 | 26.6667 | 26.6667 | 29.1667 | 31.25 | 33.3333 | 35 | 36.25 | 37.9167 | 39.1667 | 40.4167 | 41.6667 | 42.9167 | 43.75 | 45 | 45.8333 | 46.6667 | 47.5 | 48.3333 | 49.1667 | 50 | 51.6667 | 52.9167 | 54.1667 | 55.4167 | 56.25 | 58.75 | 60.8333 | 62.9167
34.5 | 25.4167 | 25.4167 | 27.9167 | 29.5833 | 32.5 | 32.9167 | 34.5833 | 35.8333 | 37.5 | 38.3333 | 39.5833 | 40.8333 | 41.6667 | 42.5 | 43.75 | 44.5833 | 45.4167 | 46.25 | 46.6667 | 47.5 | 49.1667 | 50.4167 | 51.25 | 52.5 | 53.75 | 55.8333 | 57.9167 | 60
34.6 | 24.1667 | 24.1667 | 26.25 | 27.9167 | 30 | 31.25 | 32.9167 | 34.1667 | 35.4167 | 36.6667 | 37.5 | 38.75 | 39.5833 | 40.4167 | 41.25 | 42.0833 | 42.9167 | 43.75 | 44.5833 | 44.1667 | 46.6667 | 47.5 | 48.75 | 50 | 50.8333 | 53.3333 | 55 | 57.0833
34.7 | 22.5 | 22.5 | 24.5833 | 26.6667 | 27.9167 | 29.5833 | 30.8333 | 32.0833 | 33.3333 | 34.5833 | 35.4167 | 36.6667 | 37.5 | 38.3333 | 39.1667 | 40 | 40.8333 | 41.25 | 42.0833 | 42.5 | 43.75 | 45 | 46.25 | 47.0833 | 48.3333 | 50.4167 | 52.0833 | 53.75
34.8 | 21.25 | 21.25 | 23.3333 | 25 | 26.25 | 27.9167 | 29.1667 | 30.4167 | 31.25 | 32.5 | 33.3333 | 34.1667 | 35 | 36.6667 | 36.6667 | 37.5 | 38.3333 | 38.75 | 39.5833 | 40.4167 | 41.25 | 42.5 | 43.3333 | 44.5833 | 45.4167 | 47.5 | 49.1667 | 50.8333
34.9 | 20 | 20 | 21.6667 | 23.3333 | 24.5833 | 26.25 | 27.0833 | 28.3333 | 29.5833 | 30.4167 | 31.25 | 32.0833 | 32.5 | 33.75 | 34.5833 | 35.4167 | 35.8333 | 36.6667 | 37.0833 | 37.9167 | 38.75 | 40 | 40.8333 | 41.6667 | 42.5 | 44.5833 | 46.25 | 47.9167
DO NOT EDIT THIS SHEET!!!

## B
17 | 2 | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A |  |  | THIS HAS BEEN FIXED
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
#N/A | #N/A | #N/A | #N/A | #N/A
0.1 | 1 | 0.1 | 1 | 0.1 | 1 | 0.1 | 1 | 0.1 | 1
0.2 | 2 | 0.2 | 2 | 0.2 | 2 | 0.2 | 2 | 0.2 | 2
0.3 | 3 | 0.3 | 3 | 0.3 | 3 | 0.3 | 3 | 0.3 | 3
0.4 | 4 | 0.4 | 4 | 0.4 | 4 | 0.4 | 4 | 0.4 | 4
0.5 | 5 | 0.5 | 5 | 0.5 | 5 | 0.5 | 5 | 0.5 | 5
0.6 | 6 | 0.6 | 6 | 0.6 | 6 | 0.6 | 6 | 0.6 | 6
0.7 | 7 | 0.7 | 7 | 0.7 | 7 | 0.7 | 7 | 0.7 | 7
0.8 | 8 | 0.8 | 8 | 0.8 | 8 | 0.8 | 8 | 0.8 | 8
0.9 | 9 | 0.9 | 9 | 0.9 | 9 | 0.9 | 9 | 0.9 | 9
1 | 10 | 1 | 10 | 1 | 10 | 1 | 10 | 1 | 10
1.1 | 11 | 1.1 | 11 | 1.1 | 11 | 1.1 | 11 | 1.1 | 11
1.2 | 12 | 1.2 | 12 | 1.2 | 12 | 1.2 | 12 | 1.2 | 12
1.3 | 13 | 1.3 | 13 | 1.3 | 13 | 1.3 | 13 | 1.3 | 13
1.4 | 14 | 1.4 | 14 | 1.4 | 14 | 1.4 | 14 | 1.4 | 14
1.5 | 15 | 1.5 | 15 | 1.5 | 15 | 1.5 | 15 | 1.5 | 15
1.6 | 16 | 1.6 | 16 | 1.6 | 16 | 1.6 | 16 | 1.6 | 16
1.7 | 17 | 1.7 | 17 | 1.7 | 17 | 1.7 | 17 | 1.7 | 17
1.8 | 18 | 1.8 | 18 | 1.8 | 18 | 1.8 | 18 | 1.8 | 18
1.9 | 19 | 1.9 | 19 | 1.9 | 19 | 1.9 | 19 | 1.9 | 19
2 | 20 | 2 | 20 | 2 | 20 | 2 | 20 | 2 | 20
2.2 | 21 | 2.2 | 21 | 2.2 | 21 | 2.2 | 21 | 2.2 | 21
2.4 | 22 | 2.4 | 22 | 2.4 | 22 | 2.4 | 22 | 2.4 | 22
2.6 | 23 | 2.6 | 23 | 2.6 | 23 | 2.6 | 23 | 2.6 | 23
2.8 | 24 | 2.8 | 24 | 2.8 | 24 | 2.8 | 24 | 2.8 | 24
3 | 25 | 3 | 25 | 3 | 25 | 3 | 25 | 3 | 25
3.5 | 26 | 3.5 | 26 | 3.5 | 26 | 3.5 | 26 | 3.5 | 26
4 | 27 | 4 | 27 | 4 | 27 | 4 | 27 | 4 | 27
4.5 | 28 | 4.5 | 28 | 4.5 | 28 | 4.5 | 28 | 4.5 | 28

## DATA
SCP Chart
Velocity (m/s)
|  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.2 | 2.4 | 2.6 | 2.8 | 3 | 3.5 | 4 | 4.5
Wetbulb Temperature (°C) | 20 | 376 | 376 | 381 | 394 | 405 | 415 | 424 | 432 | 439 | 446 | 452 | 457 | 462 | 467 | 472 | 476 | 480 | 484 | 487 | 491 | 497 | 503 | 508 | 513 | 517 | 527 | 535 | 542 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 20.1 | 375 | 375 | 380 | 393 | 404 | 414 | 423 | 431 | 438 | 445 | 451 | 456 | 461 | 466 | 471 | 475 | 479 | 483 | 486 | 490 | 496 | 502 | 507 | 512 | 516 | 526 | 534 | 541 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 20.2 | 373 | 373 | 378 | 391 | 402 | 412 | 421 | 429 | 436 | 443 | 449 | 454 | 459 | 464 | 469 | 473 | 477 | 481 | 484 | 488 | 494 | 500 | 505 | 510 | 514 | 524 | 532 | 539 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 20.3 | 371 | 371 | 376 | 389 | 400 | 410 | 419 | 427 | 434 | 441 | 447 | 452 | 457 | 462 | 467 | 471 | 475 | 479 | 482 | 486 | 492 | 498 | 503 | 508 | 512 | 522 | 530 | 537 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 20.4 | 370 | 370 | 375 | 388 | 399 | 409 | 418 | 426 | 433 | 440 | 446 | 451 | 456 | 461 | 466 | 470 | 474 | 478 | 481 | 485 | 491 | 497 | 502 | 507 | 511 | 521 | 529 | 536 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 20.5 | 369 | 369 | 374 | 387 | 398 | 408 | 417 | 425 | 432 | 439 | 445 | 450 | 455 | 460 | 465 | 469 | 473 | 477 | 480 | 484 | 490 | 496 | 501 | 506 | 510 | 520 | 528 | 535 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 20.6 | 367 | 367 | 372 | 385 | 396 | 406 | 415 | 423 | 430 | 437 | 443 | 448 | 453 | 458 | 463 | 467 | 471 | 475 | 478 | 482 | 488 | 494 | 499 | 504 | 508 | 518 | 526 | 533 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 20.7 | 365 | 365 | 370 | 383 | 394 | 404 | 413 | 421 | 428 | 435 | 441 | 446 | 451 | 456 | 461 | 465 | 469 | 473 | 476 | 480 | 486 | 492 | 497 | 502 | 506 | 516 | 524 | 531 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 20.8 | 364 | 364 | 369 | 382 | 393 | 403 | 412 | 420 | 427 | 434 | 440 | 445 | 450 | 455 | 460 | 464 | 468 | 472 | 475 | 479 | 485 | 491 | 496 | 501 | 505 | 515 | 523 | 530 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 20.9 | 363 | 363 | 368 | 381 | 392 | 402 | 411 | 419 | 426 | 433 | 439 | 444 | 449 | 454 | 459 | 463 | 467 | 471 | 474 | 478 | 484 | 490 | 495 | 500 | 504 | 514 | 522 | 529 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 21 | 361 | 361 | 366 | 379 | 390 | 400 | 409 | 417 | 424 | 431 | 437 | 442 | 447 | 452 | 457 | 461 | 465 | 469 | 472 | 476 | 482 | 488 | 493 | 498 | 502 | 512 | 520 | 527 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 21.1 | 359 | 359 | 364 | 377 | 388 | 398 | 407 | 415 | 422 | 429 | 435 | 440 | 445 | 450 | 455 | 459 | 463 | 467 | 470 | 474 | 480 | 486 | 491 | 496 | 500 | 510 | 518 | 525 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 21.2 | 358 | 358 | 363 | 376 | 387 | 397 | 406 | 414 | 421 | 428 | 434 | 439 | 444 | 449 | 454 | 458 | 462 | 466 | 469 | 473 | 479 | 485 | 490 | 495 | 499 | 509 | 517 | 524 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 21.3 | 357 | 357 | 362 | 375 | 386 | 396 | 405 | 413 | 420 | 427 | 433 | 438 | 443 | 448 | 453 | 457 | 461 | 465 | 468 | 472 | 478 | 484 | 489 | 494 | 498 | 508 | 516 | 523 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 21.4 | 355 | 355 | 360 | 373 | 384 | 394 | 403 | 411 | 418 | 425 | 431 | 436 | 441 | 446 | 451 | 455 | 459 | 463 | 466 | 470 | 476 | 482 | 487 | 492 | 496 | 506 | 514 | 521 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 21.5 | 353 | 353 | 358 | 371 | 382 | 392 | 401 | 409 | 416 | 423 | 429 | 434 | 439 | 444 | 449 | 453 | 457 | 461 | 464 | 468 | 474 | 480 | 485 | 490 | 494 | 504 | 512 | 519 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 21.6 | 352 | 352 | 357 | 370 | 381 | 391 | 400 | 408 | 415 | 422 | 428 | 433 | 438 | 443 | 448 | 452 | 456 | 460 | 463 | 467 | 473 | 479 | 484 | 489 | 493 | 503 | 511 | 518 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 21.7 | 351 | 351 | 356 | 369 | 380 | 390 | 399 | 407 | 414 | 421 | 427 | 432 | 437 | 442 | 447 | 451 | 455 | 459 | 462 | 466 | 472 | 478 | 483 | 488 | 492 | 502 | 510 | 517 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 21.8 | 349 | 349 | 354 | 367 | 378 | 388 | 397 | 405 | 412 | 419 | 425 | 430 | 435 | 440 | 445 | 449 | 453 | 457 | 460 | 464 | 470 | 476 | 481 | 486 | 490 | 500 | 508 | 515 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 21.9 | 347 | 347 | 352 | 365 | 376 | 386 | 395 | 403 | 410 | 417 | 423 | 428 | 433 | 438 | 443 | 447 | 451 | 455 | 458 | 462 | 468 | 474 | 479 | 484 | 488 | 498 | 506 | 513 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 22 | 346 | 346 | 351 | 364 | 375 | 385 | 394 | 402 | 409 | 416 | 422 | 427 | 432 | 437 | 442 | 446 | 450 | 454 | 457 | 461 | 467 | 473 | 478 | 483 | 487 | 497 | 505 | 512 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 22.1 | 345 | 345 | 350 | 363 | 374 | 384 | 393 | 401 | 408 | 415 | 421 | 426 | 431 | 436 | 441 | 445 | 449 | 453 | 456 | 460 | 466 | 472 | 477 | 482 | 486 | 496 | 504 | 511 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 22.2 | 343 | 343 | 348 | 361 | 372 | 382 | 391 | 399 | 406 | 413 | 419 | 424 | 429 | 434 | 439 | 443 | 447 | 451 | 454 | 458 | 464 | 470 | 475 | 480 | 484 | 494 | 502 | 509 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 22.3 | 341 | 341 | 346 | 359 | 370 | 380 | 389 | 397 | 404 | 411 | 417 | 422 | 427 | 432 | 437 | 441 | 445 | 449 | 452 | 456 | 462 | 468 | 473 | 478 | 482 | 492 | 500 | 507 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 22.4 | 340 | 340 | 345 | 358 | 369 | 379 | 388 | 396 | 403 | 410 | 416 | 421 | 426 | 431 | 436 | 440 | 444 | 448 | 451 | 455 | 461 | 467 | 472 | 477 | 481 | 491 | 499 | 506 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 22.5 | 339 | 339 | 344 | 357 | 368 | 378 | 387 | 395 | 402 | 409 | 415 | 420 | 425 | 430 | 435 | 439 | 443 | 447 | 450 | 454 | 460 | 466 | 471 | 476 | 480 | 490 | 498 | 505 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 22.6 | 337 | 337 | 342 | 355 | 366 | 376 | 385 | 393 | 400 | 407 | 413 | 418 | 423 | 428 | 433 | 437 | 441 | 445 | 448 | 452 | 458 | 464 | 469 | 474 | 478 | 488 | 496 | 503 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 22.7 | 335 | 335 | 340 | 353 | 364 | 374 | 383 | 391 | 398 | 405 | 411 | 416 | 421 | 426 | 431 | 435 | 439 | 443 | 446 | 450 | 456 | 462 | 467 | 472 | 476 | 486 | 494 | 501 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 22.8 | 334 | 334 | 339 | 352 | 363 | 373 | 382 | 390 | 397 | 404 | 410 | 415 | 420 | 425 | 430 | 434 | 438 | 442 | 445 | 449 | 455 | 461 | 466 | 471 | 475 | 485 | 493 | 500 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 22.9 | 333 | 333 | 338 | 351 | 362 | 372 | 381 | 389 | 396 | 403 | 409 | 414 | 419 | 424 | 429 | 433 | 437 | 441 | 444 | 448 | 454 | 460 | 465 | 470 | 474 | 484 | 492 | 499 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 23 | 331 | 331 | 336 | 349 | 360 | 370 | 379 | 387 | 394 | 401 | 407 | 412 | 417 | 422 | 427 | 431 | 435 | 439 | 442 | 446 | 452 | 458 | 463 | 468 | 472 | 482 | 490 | 497 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 23.1 | 329 | 329 | 334 | 347 | 358 | 368 | 377 | 385 | 392 | 399 | 405 | 410 | 415 | 420 | 425 | 429 | 433 | 437 | 440 | 444 | 450 | 456 | 461 | 466 | 470 | 480 | 488 | 495 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 23.2 | 328 | 328 | 333 | 346 | 357 | 367 | 376 | 384 | 391 | 398 | 404 | 409 | 414 | 419 | 424 | 428 | 432 | 436 | 439 | 443 | 449 | 455 | 460 | 465 | 469 | 479 | 487 | 494 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 23.3 | 326 | 326 | 331 | 344 | 355 | 365 | 374 | 382 | 389 | 396 | 402 | 407 | 412 | 417 | 422 | 426 | 430 | 434 | 437 | 441 | 447 | 453 | 458 | 463 | 467 | 477 | 485 | 492 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 23.4 | 324 | 324 | 329 | 342 | 353 | 363 | 372 | 380 | 387 | 394 | 400 | 405 | 410 | 415 | 420 | 424 | 428 | 432 | 435 | 439 | 445 | 451 | 456 | 461 | 465 | 475 | 483 | 490 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 23.5 | 323 | 323 | 328 | 341 | 352 | 362 | 371 | 379 | 386 | 393 | 399 | 404 | 409 | 414 | 419 | 423 | 427 | 431 | 434 | 438 | 444 | 450 | 455 | 460 | 464 | 474 | 482 | 489 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 23.6 | 322 | 322 | 327 | 340 | 351 | 361 | 370 | 378 | 385 | 392 | 398 | 403 | 408 | 413 | 418 | 422 | 426 | 430 | 433 | 437 | 443 | 449 | 454 | 459 | 463 | 473 | 481 | 488 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 23.7 | 320 | 320 | 325 | 338 | 349 | 359 | 368 | 376 | 383 | 390 | 396 | 401 | 406 | 411 | 416 | 420 | 424 | 428 | 431 | 435 | 441 | 447 | 452 | 457 | 461 | 471 | 479 | 486 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 23.8 | 318 | 318 | 323 | 336 | 347 | 357 | 366 | 374 | 381 | 388 | 394 | 399 | 404 | 409 | 414 | 418 | 422 | 426 | 429 | 433 | 439 | 445 | 450 | 455 | 459 | 469 | 477 | 484 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 23.9 | 317 | 317 | 322 | 335 | 346 | 356 | 365 | 373 | 380 | 387 | 393 | 398 | 403 | 408 | 413 | 417 | 421 | 425 | 428 | 432 | 438 | 444 | 449 | 454 | 458 | 468 | 476 | 483 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 24 | 315 | 315 | 320 | 333 | 344 | 354 | 363 | 371 | 378 | 385 | 391 | 396 | 401 | 406 | 411 | 415 | 419 | 423 | 426 | 430 | 436 | 442 | 447 | 452 | 456 | 466 | 474 | 481 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 24.1 | 313 | 313 | 318 | 331 | 342 | 352 | 361 | 369 | 376 | 383 | 389 | 394 | 399 | 404 | 409 | 413 | 417 | 421 | 424 | 428 | 434 | 440 | 445 | 450 | 454 | 464 | 472 | 479 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 24.2 | 312 | 312 | 317 | 330 | 341 | 351 | 360 | 368 | 375 | 382 | 388 | 393 | 398 | 403 | 408 | 412 | 416 | 420 | 423 | 427 | 433 | 439 | 444 | 449 | 453 | 463 | 471 | 478 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
| 24.3 | 311 | 311 | 316 | 329 | 340 | 350 | 359 | 367 | 374 | 381 | 387 | 392 | 397 | 402 | 407 | 411 | 415 | 419 | 422 | 426 | 432 | 438 | 443 | 448 | 452 | 462 | 470 | 477 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 24.4 | 309 | 309 | 314 | 327 | 338 | 348 | 357 | 365 | 372 | 379 | 385 | 390 | 395 | 400 | 405 | 409 | 413 | 417 | 420 | 424 | 430 | 436 | 441 | 446 | 450 | 460 | 468 | 475 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2
| 24.5 | 307 | 307 | 312 | 325 | 336 | 346 | 355 | 363 | 370 | 377 | 383 | 388 | 393 | 398 | 403 | 407 | 411 | 415 | 418 | 422 | 428 | 434 | 439 | 444 | 448 | 458 | 466 | 473 | -1 | -1 | -1.5 | -1 | -1 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -2 | -2 | -2
| 24.6 | 306 | 306 | 311 | 324 | 335 | 345 | 354 | 362 | 389 | 376 | 382 | 387 | 392 | 397 | 402 | 406 | 410 | 414 | 417 | 421 | 427 | 433 | 438 | 443 | 447 | 457 | 465 | 472 | -2 | -2 | -1.5 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2.5 | -2.5 | -2 | -2 | -2.5 | -2 | -2 | -2 | -2
| 24.7 | 304 | 304 | 309 | 322 | 333 | 343 | 352 | 360.5 | 387 | 374 | 380 | 385 | 390 | 395 | 400 | 404 | 408 | 411.5 | 415 | 419 | 425 | 431 | 435.5 | 441 | 444.5 | 455 | 462.5 | 469.5 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -1.5 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2.5 | -2 | -2 | -2 | -2 | -2.5 | -2 | -2.5 | -2 | -2.5 | -2.5
| 24.8 | 303 | 303 | 307.5 | 320.5 | 331.5 | 342 | 350.5 | 359 | 385.5 | 372.5 | 378.5 | 383.5 | 388.5 | 393 | 398.5 | 402.5 | 406.5 | 410 | 413.5 | 417.5 | 423.5 | 429 | 434 | 439.5 | 443 | 453 | 461 | 468 | -1 | -1 | -1.5 | -1.5 | -1.5 | -1 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -2 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -1.5 | -2 | -1.5 | -1.5 | -1.5 | -2 | -1.5 | -1.5
| 24.9 | 301 | 301 | 305.5 | 319 | 329.5 | 340 | 348.5 | 357 | 383.5 | 370.5 | 376 | 381.5 | 386.5 | 391 | 396.5 | 400.5 | 404 | 408 | 411 | 415.5 | 421 | 427 | 432 | 437 | 441 | 451 | 458.5 | 465.5 | -2 | -2 | -2 | -1.5 | -2 | -2 | -2 | -2 | -2 | -2 | -2.5 | -2 | -2 | -2 | -2 | -2 | -2.5 | -2 | -2.5 | -2 | -2.5 | -2 | -2 | -2.5 | -2 | -2 | -2.5 | -2.5
| 25 | 299 | 299 | 304 | 317 | 328 | 338 | 346.5 | 355 | 382 | 368.5 | 374 | 379.5 | 384.5 | 389 | 394 | 398 | 402 | 406 | 409 | 413 | 419 | 425 | 429.5 | 435 | 438.5 | 448.5 | 456.5 | 463.5 | -2 | -2 | -1.5 | -2 | -1.5 | -2 | -2 | -2 | -1.5 | -2 | -2 | -2 | -2 | -2 | -2.5 | -2.5 | -2 | -2 | -2 | -2.5 | -2 | -2 | -2.5 | -2 | -2.5 | -2.5 | -2 | -2
| 25.1 | 294 | 294 | 309 | 322 | 333 | 343 | 352 | 360 | 367 | 374 | 380 | 385 | 390 | 395 | 400 | 404 | 408 | 412 | 415 | 419 | 425 | 430 | 436 | 440 | 445 | 454 | 462 | 469 | -1 | -1 | -1 | -1 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -2 | -3 | -2 | -3 | -2 | -2 | -2
| 25.2 | 293 | 293 | 308 | 321 | 332 | 341 | 350 | 358 | 365 | 372 | 378 | 383 | 388 | 393 | 398 | 402 | 406 | 409 | 413 | 416 | 423 | 428 | 433 | 438 | 442 | 452 | 460 | 467 | -2 | -2 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | 1 | -2 | -2 | -2
| 25.3 | 291 | 291 | 306 | 319 | 330 | 340 | 348 | 356 | 363 | 370 | 376 | 381 | 386 | 391 | 395 | 400 | 404 | 407 | 411 | 414 | 420 | 426 | 431 | 436 | 443 | 450 | 458 | 465 | -1 | -1 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -5 | -3 | -3 | -3
| 25.4 | 290 | 290 | 305 | 317 | 328 | 338 | 346 | 354 | 361 | 368 | 374 | 379 | 384 | 388 | 393 | 398 | 401 | 405 | 409 | 412 | 418 | 424 | 429 | 433 | 438 | 447 | 455 | 462 | -2 | -2 | -2 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -1 | -2 | -3 | -2 | -2 | -3 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -2 | -2
| 25.5 | 288 | 288 | 303 | 315 | 326 | 336 | 345 | 352 | 359 | 366 | 372 | 377 | 382 | 387 | 391 | 395 | 399 | 403 | 406 | 410 | 416 | 421 | 426 | 431 | 435 | 445 | 453 | 460 | -1 | -1 | -2 | -1 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3
| 25.6 | 287 | 287 | 301 | 314 | 325 | 334 | 343 | 350 | 357 | 364 | 370 | 375 | 380 | 385 | 389 | 393 | 397 | 401 | 404 | 408 | 414 | 419 | 424 | 429 | 433 | 442 | 450 | 457 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -2 | -3 | -2 | -2 | -2 | -2
| 25.7 | 285 | 285 | 300 | 312 | 323 | 332 | 341 | 348 | 355 | 362 | 368 | 373 | 378 | 383 | 387 | 391 | 395 | 399 | 402 | 405 | 411 | 417 | 422 | 426 | 431 | 440 | 448 | 455 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -3 | -3
| 25.8 | 283 | 283 | 298 | 310 | 321 | 330 | 339 | 347 | 353 | 360 | 366 | 371 | 376 | 381 | 385 | 389 | 393 | 396 | 400 | 403 | 409 | 415 | 419 | 424 | 428 | 438 | 445 | 452 | -1 | -1 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -2
| 25.9 | 282 | 282 | 296 | 308 | 319 | 329 | 337 | 345 | 351 | 358 | 364 | 369 | 374 | 378 | 383 | 387 | 391 | 394 | 398 | 401 | 407 | 412 | 417 | 422 | 426 | 435 | 443 | 450 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -3 | -2 | -2 | -3 | -2 | -2 | -3 | -3
| 26 | 280 | 280 | 294 | 307 | 317 | 327 | 335 | 343 | 349 | 356 | 361 | 367 | 372 | 376 | 381 | 385 | 388 | 392 | 395 | 399 | 404 | 410 | 415 | 419 | 424 | 433 | 440 | 447 | -2 | -2 | -1 | -2 | -1 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -2 | -2
| 26.1 | 278 | 278 | 293 | 305 | 316 | 325 | 333 | 341 | 348 | 354 | 359 | 365 | 370 | 374 | 378 | 382 | 386 | 390 | 393 | 396 | 402 | 408 | 412 | 417 | 421 | 430 | 438 | 445 | -1 | -1 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -3
| 26.2 | 277 | 277 | 290 | 303 | 314 | 323 | 331 | 339 | 346 | 352 | 357 | 363 | 367 | 372 | 376 | 380 | 384 | 388 | 391 | 394 | 400 | 405 | 410 | 415 | 419 | 428 | 435 | 442 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -2 | -2
| 26.3 | 275 | 275 | 289 | 301 | 312 | 321 | 329 | 337 | 343 | 350 | 355 | 361 | 365 | 370 | 374 | 378 | 382 | 385 | 389 | 392 | 398 | 403 | 408 | 412 | 416 | 425 | 433 | 440 | -1 | -1 | -1 | -1 | -2 | -2 | -2 | -4 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | 0 | -2 | -2 | -3 | -3 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -3
| 26.4 | 274 | 274 | 288 | 300 | 310 | 319 | 327 | 333 | 341 | 348 | 353 | 358 | 363 | 368 | 372 | 378 | 380 | 383 | 386 | 389 | 395 | 401 | 405 | 410 | 414 | 423 | 430 | 437 | -2 | -2 | -2 | -2 | -4 | -2 | -2 | 0 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -4 | -3 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -3
| 26.5 | 272 | 272 | 286 | 298 | 306 | 317 | 325 | 333 | 339 | 346 | 351 | 356 | 361 | 366 | 370 | 374 | 377 | 381 | 384 | 387 | 393 | 398 | 403 | 407 | 411 | 420 | 428 | 434 | -2 | -2 | -2 | -2 | 0 | -2 | -1 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2
| 26.6 | 270 | 270 | 284 | 296 | 306 | 315 | 324 | 330 | 337 | 343 | 349 | 354 | 359 | 363 | 368 | 371 | 375 | 379 | 382 | 385 | 391 | 396 | 401 | 405 | 409 | 418 | 425 | 432 | -1 | -1 | -1 | -2 | -1 | -1 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -1 | -3 | -2 | -3 | -3 | -3 | -2 | -2 | -3 | -2 | -3
| 26.7 | 269 | 269 | 283 | 294 | 305 | 314 | 322 | 329 | 335 | 341 | 347 | 352 | 357 | 361 | 366 | 369 | 373 | 378 | 379 | 383 | 388 | 393 | 398 | 403 | 407 | 415 | 423 | 429 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -4 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -2
| 26.8 | 267 | 267 | 281 | 292 | 303 | 312 | 320 | 327 | 333 | 339 | 345 | 350 | 355 | 359 | 363 | 367 | 371 | 374 | 377 | 380 | 386 | 391 | 396 | 400 | 404 | 413 | 420 | 427 | -2 | -2 | -3 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -3
| 26.9 | 265 | 265 | 278 | 291 | 301 | 310 | 318 | 325 | 331 | 337 | 343 | 348 | 352 | 357 | 361 | 365 | 368 | 372 | 375 | 378 | 384 | 389 | 393 | 398 | 402 | 410 | 418 | 424 | -1 | -1 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | 0 | -3 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -2 | -3 | -3
| 27 | 264 | 264 | 277 | 289 | 299 | 308 | 316 | 323 | 329 | 335 | 341 | 346 | 350 | 355 | 359 | 362 | 368 | 369 | 373 | 376 | 381 | 386 | 391 | 395 | 399 | 408 | 415 | 421 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -4 | -3 | -3 | -2 | -4 | -2 | -3 | -3 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -2
| 27.1 | 262 | 262 | 276 | 287 | 297 | 306 | 314 | 321 | 327 | 333 | 338 | 343 | 346 | 352 | 356 | 360 | 364 | 367 | 370 | 373 | 379 | 384 | 388 | 393 | 397 | 405 | 413 | 419 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | 0 | -2 | 0 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -1 | -2 | -3 | -3
| 27.2 | 260 | 260 | 274 | 285 | 295 | 304 | 312 | 319 | 325 | 331 | 338 | 341 | 346 | 350 | 354 | 358 | 361 | 365 | 368 | 371 | 376 | 381 | 386 | 390 | 396 | 403 | 410 | 416 | -1 | -1 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -4 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -2 | -4 | -3 | -3 | -3
| 27.3 | 259 | 259 | 272 | 283 | 294 | 302 | 310 | 317 | 323 | 329 | 334 | 339 | 344 | 348 | 352 | 356 | 359 | 362 | 366 | 368 | 374 | 379 | 384 | 388 | 392 | 400 | 407 | 413 | -2 | -2 | -2 | -1 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -3 | -2 | -2 | -2
| 27.4 | 257 | 257 | 270 | 282 | 291 | 300 | 308 | 315 | 321 | 327 | 332 | 337 | 341 | 346 | 350 | 353 | 357 | 360 | 363 | 366 | 372 | 377 | 381 | 385 | 389 | 398 | 405 | 411 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -2 | -2 | -2 | -3 | -3 | -3
| 27.5 | 255 | 255 | 268 | 280 | 289 | 298 | 306 | 313 | 319 | 325 | 330 | 335 | 339 | 343 | 347 | 351 | 354 | 358 | 361 | 364 | 369 | 374 | 379 | 383 | 387 | 395 | 402 | 408 | -1 | -1 | -1 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3
| 27.6 | 254 | 254 | 267 | 278 | 287 | 296 | 304 | 310 | 317 | 322 | 328 | 332 | 337 | 341 | 345 | 349 | 352 | 355 | 358 | 361 | 367 | 372 | 376 | 380 | 384 | 392 | 399 | 405 | -2 | -2 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -2 | -3 | -2 | -2 | -2
| 27.7 | 252 | 252 | 265 | 276 | 286 | 294 | 302 | 308 | 315 | 320 | 325 | 330 | 335 | 339 | 343 | 346 | 350 | 353 | 356 | 359 | 364 | 369 | 374 | 378 | 381 | 390 | 397 | 403 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -3
| 27.8 | 250 | 250 | 263 | 274 | 284 | 292 | 300 | 306 | 312 | 318 | 323 | 328 | 332 | 337 | 340 | 344 | 347 | 351 | 354 | 357 | 362 | 367 | 371 | 375 | 379 | 387 | 394 | 400 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3
| 27.9 | 248 | 248 | 261 | 272 | 282 | 290 | 298 | 304 | 310 | 316 | 321 | 326 | 330 | 334 | 338 | 342 | 345 | 348 | 351 | 354 | 359 | 364 | 369 | 373 | 376 | 385 | 391 | 397 | -1 | -1 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -2
| 28 | 247 | 247 | 259 | 270 | 280 | 288 | 295 | 302 | 308 | 314 | 319 | 324 | 328 | 332 | 336 | 339 | 343 | 346 | 349 | 352 | 357 | 362 | 366 | 370 | 374 | 382 | 389 | 395 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -3
| 28.1 | 245 | 245 | 258 | 268 | 278 | 286 | 293 | 300 | 306 | 312 | 317 | 321 | 326 | 330 | 333 | 337 | 340 | 343 | 346 | 349 | 354 | 359 | 364 | 367 | 371 | 379 | 386 | 392 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -3
| 28.2 | 243 | 243 | 256 | 266 | 276 | 284 | 291 | 298 | 304 | 309 | 314 | 319 | 323 | 327 | 331 | 335 | 338 | 341 | 344 | 347 | 352 | 357 | 361 | 365 | 369 | 377 | 383 | 389 | -2 | -2 | -2 | 0 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3
| 28.3 | 241 | 241 | 254 | 266 | 274 | 282 | 289 | 296 | 302 | 307 | 312 | 317 | 321 | 325 | 329 | 332 | 336 | 339 | 342 | 344 | 349 | 354 | 358 | 362 | 366 | 374 | 381 | 386 | -1 | -1 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -2
| 28.4 | 240 | 240 | 252 | 263 | 272 | 280 | 287 | 294 | 300 | 305 | 310 | 314 | 319 | 323 | 326 | 330 | 333 | 336 | 339 | 342 | 347 | 352 | 356 | 360 | 363 | 371 | 378 | 384 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -2 | -2 | -3 | -3
| 28.5 | 238 | 238 | 250 | 261 | 270 | 278 | 285 | 292 | 297 | 303 | 308 | 312 | 316 | 320 | 324 | 327 | 331 | 334 | 337 | 339 | 344 | 349 | 353 | 357 | 361 | 369 | 375 | 381 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -3 | -2 | -2 | -4 | -2 | -2 | -3 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3
| 28.6 | 235 | 235 | 248 | 259 | 268 | 276 | 283 | 289 | 295 | 300 | 305 | 310 | 314 | 316 | 322 | 325 | 328 | 331 | 334 | 337 | 342 | 346 | 351 | 354 | 358 | 366 | 372 | 378 | -2 | -2 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | 0 | -3 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -2 | -3
| 28.7 | 233 | 233 | 247 | 257 | 266 | 274 | 281 | 287 | 293 | 298 | 303 | 308 | 312 | 316 | 319 | 323 | 326 | 329 | 332 | 334 | 339 | 344 | 348 | 352 | 355 | 363 | 370 | 375 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -3
| 28.8 | 230 | 230 | 245 | 255 | 264 | 272 | 279 | 285 | 291 | 296 | 301 | 305 | 309 | 313 | 317 | 320 | 323 | 326 | 329 | 332 | 337 | 341 | 345 | 349 | 353 | 360 | 367 | 372 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -2 | -2 | -3 | -2 | -3 | -2
| 28.9 | 227 | 227 | 243 | 253 | 262 | 270 | 277 | 283 | 289 | 294 | 299 | 303 | 307 | 311 | 314 | 318 | 321 | 324 | 327 | 329 | 334 | 339 | 343 | 347 | 350 | 358 | 364 | 370 | -2 | -2 | -2 | -2 | 0 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 29 | 225 | 225 | 241 | 251 | 262 | 268 | 274 | 281 | 286 | 291 | 296 | 301 | 305 | 308 | 312 | 315 | 318 | 321 | 324 | 327 | 332 | 336 | 340 | 344 | 347 | 355 | 361 | 367 | -3 | -3 | -1 | -2 | -4 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -2 | -2 | -2 | 0 | -2 | -2 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3
| 29.1 | 222 | 222 | 240 | 249 | 258 | 265 | 272 | 278 | 284 | 289 | 294 | 298 | 302 | 306 | 310 | 313 | 318 | 319 | 322 | 324 | 329 | 334 | 338 | 341 | 345 | 352 | 358 | 364 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -5 | -3 | -3 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -2 | -3
| 29.2 | 220 | 220 | 237 | 247 | 256 | 263 | 270 | 276 | 282 | 287 | 292 | 296 | 300 | 304 | 307 | 310 | 313 | 316 | 319 | 322 | 327 | 331 | 335 | 339 | 342 | 349 | 356 | 361 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -3
| 29.3 | 217 | 217 | 234 | 245 | 254 | 261 | 268 | 274 | 280 | 285 | 289 | 294 | 298 | 301 | 305 | 308 | 311 | 314 | 317 | 319 | 324 | 328 | 332 | 336 | 339 | 347 | 353 | 358 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -2 | -2 | -3 | -3 | -3 | -3 | -3
| 29.4 | 214 | 214 | 231 | 243 | 252 | 259 | 266 | 272 | 277 | 282 | 287 | 291 | 295 | 299 | 302 | 305 | 308 | 311 | 314 | 317 | 321 | 326 | 330 | 333 | 336 | 344 | 350 | 355 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -3 | -2 | -3 | -5 | -3
| 29.5 | 211 | 211 | 228 | 241 | 250 | 257 | 264 | 270 | 275 | 280 | 285 | 289 | 293 | 296 | 300 | 303 | 306 | 309 | 311 | 314 | 319 | 323 | 327 | 330 | 334 | 341 | 345 | 352 | -2 | -2 | -3 | -1 | -3 | -2 | -3 | -3 | -2 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -4 | -2
| 29.6 | 209 | 209 | 225 | 240 | 247 | 255 | 261 | 267 | 273 | 278 | 282 | 286 | 290 | 294 | 297 | 300 | 303 | 306 | 309 | 311 | 316 | 320 | 324 | 328 | 331 | 338 | 341 | 350 | -3 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -2 | -2 | -2 | -4 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -1 | -3
| 29.7 | 206 | 206 | 222 | 237 | 245 | 253 | 259 | 265 | 271 | 275 | 280 | 284 | 288 | 291 | 295 | 298 | 301 | 304 | 305 | 309 | 313 | 318 | 321 | 325 | 328 | 335 | 340 | 347 | -3 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -1 | -3 | -2 | -3 | -2 | -3 | -3 | -2 | -1 | -3
| 29.8 | 203 | 203 | 219 | 234 | 243 | 251 | 257 | 263 | 268 | 273 | 277 | 282 | 285 | 289 | 292 | 295 | 298 | 301 | 304 | 306 | 311 | 315 | 319 | 322 | 325 | 333 | 339 | 344 | -2 | -2 | -3 | -4 | -2 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -3
| 29.9 | 201 | 201 | 216 | 230 | 241 | 248 | 255 | 261 | 266 | 271 | 275 | 279 | 283 | 286 | 290 | 293 | 296 | 299 | 301 | 304 | 308 | 312 | 316 | 319 | 323 | 330 | 336 | 341 | -3 | -3 | -3 | -3 | -1 | -2 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3
| 30 | 198 | 198 | 213 | 227 | 240 | 246 | 253 | 258 | 264 | 268 | 273 | 277 | 281 | 284 | 287 | 290 | 293 | 296 | 298 | 301 | 305 | 310 | 313 | 317 | 320 | 327 | 333 | 338 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -3 | -2 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3
| 30.1 | 195 | 195 | 210 | 224 | 237 | 244 | 250 | 256 | 261 | 266 | 270 | 274 | 278 | 282 | 285 | 288 | 291 | 293 | 296 | 298 | 303 | 307 | 311 | 314 | 317 | 324 | 330 | 335 | -3 | -3 | -3 | -3 | -4 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 30.2 | 192 | 192 | 207 | 221 | 233 | 242 | 248 | 254 | 259 | 264 | 268 | 272 | 276 | 279 | 282 | 285 | 288 | 291 | 293 | 296 | 300 | 304 | 308 | 311 | 314 | 321 | 327 | 332 | -3 | -3 | -3 | -3 | -3 | -2 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 30.3 | 189 | 189 | 204 | 218 | 230 | 240 | 246 | 252 | 257 | 261 | 265 | 269 | 273 | 276 | 280 | 283 | 285 | 288 | 291 | 293 | 297 | 301 | 305 | 308 | 311 | 318 | 324 | 329 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -2 | -2 | -2 | -2 | -2 | -3 | -3 | -2 | -3 | -3 | -3 | -2 | -2 | -3 | -2 | -2 | -3 | -3 | -3
| 30.4 | 187 | 187 | 201 | 215 | 228 | 237 | 244 | 249 | 254 | 259 | 263 | 267 | 271 | 274 | 277 | 280 | 283 | 285 | 288 | 290 | 295 | 299 | 302 | 306 | 309 | 315 | 321 | 326 | -3 | -3 | -5 | -4 | -5 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 30.5 | 184 | 184 | 196 | 211 | 223 | 234 | 241 | 247 | 252 | 256 | 261 | 264 | 268 | 271 | 275 | 277 | 280 | 283 | 285 | 288 | 292 | 296 | 299 | 303 | 306 | 312 | 318 | 323 | -3 | -3 | -1 | -3 | -3 | -4 | -1 | -2 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -3
| 30.6 | 181 | 181 | 195 | 208 | 220 | 230 | 240 | 245 | 249 | 254 | 258 | 262 | 266 | 269 | 272 | 275 | 278 | 280 | 283 | 285 | 289 | 293 | 297 | 300 | 303 | 309 | 315 | 320 | -3 | -3 | -3 | -3 | -4 | -3 | -4 | -3 | -2 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -2
| 30.7 | 178 | 178 | 192 | 205 | 216 | 227 | 236 | 242 | 247 | 252 | 256 | 259 | 263 | 266 | 269 | 272 | 275 | 277 | 280 | 282 | 286 | 290 | 294 | 297 | 300 | 307 | 312 | 318 | -3 | -3 | -3 | -3 | -3 | -4 | -3 | -2 | -2 | -3 | -3 | -2 | -3 | -2 | -2 | -2 | -3 | -2 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -4 | -4
| 30.8 | 175 | 175 | 189 | 202 | 213 | 223 | 233 | 240 | 245 | 249 | 253 | 257 | 260 | 264 | 267 | 270 | 272 | 275 | 277 | 279 | 284 | 287 | 291 | 294 | 297 | 304 | 308 | 314 | -3 | -3 | -3 | -4 | -4 | -3 | -4 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -4
| 30.9 | 172 | 172 | 186 | 198 | 209 | 220 | 229 | 237 | 242 | 247 | 251 | 254 | 258 | 261 | 264 | 267 | 270 | 272 | 274 | 277 | 281 | 285 | 288 | 291 | 294 | 301 | 306 | 310 | -2 | -2 | -3 | -3 | -3 | -4 | -4 | -4 | -2 | -3 | -3 | -2 | -3 | -2 | -2 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -1 | -3 | -3 | -3 | -2
| 31 | 170 | 170 | 183 | 195 | 206 | 216 | 225 | 233 | 240 | 244 | 248 | 252 | 255 | 259 | 262 | 264 | 267 | 269 | 272 | 274 | 278 | 282 | 285 | 290 | 291 | 298 | 303 | 308 | -3 | -3 | -3 | -3 | -3 | -4 | -4 | -3 | -3 | -2 | -2 | -3 | -2 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -5 | -3 | -3 | -3 | -3
| 31.1 | 167 | 167 | 180 | 192 | 203 | 212 | 221 | 230 | 237 | 242 | 246 | 249 | 253 | 256 | 259 | 262 | 264 | 267 | 269 | 271 | 275 | 279 | 282 | 285 | 288 | 295 | 300 | 305 | -3 | -3 | -3 | -3 | -4 | -3 | -4 | -4 | -4 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -2 | -3 | -2 | -2 | -3 | -3 | -3 | -4
| 31.2 | 164 | 164 | 177 | 189 | 199 | 209 | 217 | 226 | 233 | 239 | 243 | 247 | 250 | 253 | 256 | 259 | 262 | 264 | 266 | 268 | 273 | 276 | 280 | 283 | 285 | 292 | 297 | 301 | -3 | -3 | -3 | -4 | -3 | -4 | -3 | -4 | -4 | -1 | -2 | -3 | -2 | -2 | -2 | -3 | -3 | -3 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 31.3 | 161 | 161 | 174 | 185 | 196 | 205 | 214 | 222 | 229 | 238 | 241 | 244 | 248 | 251 | 254 | 256 | 259 | 261 | 264 | 266 | 270 | 273 | 277 | 280 | 282 | 289 | 294 | 298 | -3 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -6 | -3 | -2 | -3 | -3 | -3 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -3
| 31.4 | 158 | 158 | 171 | 182 | 192 | 201 | 210 | 218 | 225 | 232 | 238 | 242 | 245 | 248 | 251 | 254 | 256 | 259 | 261 | 263 | 267 | 270 | 274 | 277 | 280 | 286 | 291 | 295 | -3 | -3 | -4 | -3 | -3 | -5 | -4 | -4 | -4 | -4 | -4 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3
| 31.5 | 155 | 155 | 167 | 179 | 189 | 196 | 206 | 214 | 221 | 228 | 234 | 239 | 242 | 245 | 248 | 251 | 253 | 256 | 258 | 260 | 264 | 268 | 271 | 274 | 277 | 283 | 288 | 292 | -3 | -3 | -3 | -4 | -4 | -2 | -4 | -4 | -4 | -4 | -4 | -3 | -2 | -2 | -2 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 31.6 | 152 | 152 | 164 | 175 | 185 | 194 | 202 | 210 | 217 | 224 | 230 | 236 | 240 | 243 | 246 | 248 | 251 | 253 | 255 | 257 | 261 | 265 | 268 | 271 | 274 | 280 | 285 | 289 | -3 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -3 | -3 | -3 | -3 | -5 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -4 | -4 | -4
| 31.7 | 149 | 149 | 161 | 172 | 181 | 190 | 198 | 206 | 213 | 219 | 225 | 231 | 237 | 240 | 243 | 245 | 246 | 250 | 252 | 254 | 258 | 262 | 265 | 268 | 271 | 276 | 281 | 285 | -3 | -3 | -3 | -4 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -3 | -3 | -2 | -1 | -3 | -2 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -2
| 31.8 | 146 | 146 | 158 | 168 | 178 | 187 | 194 | 202 | 209 | 215 | 221 | 227 | 232 | 237 | 240 | 243 | 245 | 247 | 250 | 252 | 255 | 259 | 262 | 265 | 268 | 273 | 278 | 283 | -3 | -3 | -3 | -3 | -4 | -4 | -3 | -4 | -5 | -4 | -4 | -5 | -5 | -5 | -3 | -3 | -3 | -2 | -3 | -3 | -2 | -3 | -3 | -3 | -3 | -2 | -3 | -4
| 31.9 | 143 | 143 | 155 | 165 | 174 | 183 | 191 | 198 | 204 | 211 | 217 | 222 | 227 | 232 | 237 | 240 | 242 | 245 | 247 | 249 | 253 | 256 | 259 | 262 | 265 | 271 | 275 | 279 | -3 | -3 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -5 | -5 | -4 | -4 | -4 | -5 | -3 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -4 | -4 | -3 | -3
| 32 | 140 | 140 | 152 | 162 | 171 | 179 | 187 | 194 | 200 | 206 | 212 | 218 | 223 | 228 | 232 | 237 | 240 | 242 | 244 | 246 | 250 | 253 | 256 | 259 | 261 | 267 | 272 | 276 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -4 | -5 | -4 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 32.1 | 137 | 137 | 148 | 158 | 167 | 175 | 183 | 190 | 196 | 202 | 208 | 213 | 218 | 223 | 228 | 232 | 236 | 239 | 241 | 243 | 247 | 250 | 253 | 256 | 258 | 264 | 269 | 273 | -3 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -4 | -4 | -5 | -5 | -5 | -5 | -4 | -2 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3
| 32.2 | 134 | 134 | 145 | 155 | 163 | 171 | 179 | 186 | 192 | 198 | 203 | 209 | 214 | 218 | 223 | 227 | 231 | 235 | 239 | 240 | 244 | 247 | 250 | 253 | 255 | 261 | 266 | 270 | -3 | -3 | -3 | -4 | -3 | -3 | -4 | -5 | -4 | -5 | -7 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -4 | -3
| 32.3 | 131 | 131 | 142 | 151 | 160 | 168 | 175 | 181 | 188 | 193 | 196 | 204 | 209 | 213 | 218 | 222 | 226 | 230 | 233 | 237 | 241 | 244 | 247 | 250 | 252 | 258 | 262 | 267 | -3 | -2 | -3 | -3 | -2 | -4 | -4 | -4 | -5 | -4 | -2 | -5 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -4
| 32.4 | 128 | 129 | 139 | 148 | 158 | 164 | 171 | 177 | 183 | 189 | 194 | 199 | 204 | 209 | 213 | 217 | 221 | 225 | 228 | 232 | 238 | 241 | 244 | 247 | 249 | 255 | 259 | 263 | -3 | -4 | -4 | -4 | -5 | -4 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -4 | -5 | -3 | -3 | -3 | -3 | -3 | -1 | -3
| 32.5 | 125 | 125 | 135 | 144 | 153 | 160 | 167 | 173 | 179 | 185 | 190 | 195 | 199 | 204 | 208 | 212 | 216 | 219 | 223 | 228 | 233 | 238 | 241 | 244 | 246 | 252 | 258 | 260 | -3 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -7 | -6 | -5 | -3 | -3 | -3 | -4 | -5 | -3
| 32.6 | 122 | 122 | 132 | 141 | 149 | 156 | 163 | 169 | 175 | 180 | 185 | 190 | 195 | 199 | 203 | 207 | 211 | 214 | 218 | 221 | 227 | 233 | 238 | 241 | 243 | 248 | 253 | 257 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -5 | -5 | -4 | -4 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -6 | -5 | -5 | -6 | -6 | -4 | -3 | -3 | -3 | -4
| 32.7 | 119 | 119 | 129 | 137 | 145 | 152 | 159 | 164 | 170 | 176 | 181 | 185 | 190 | 194 | 198 | 202 | 205 | 209 | 212 | 216 | 222 | 227 | 232 | 237 | 240 | 245 | 250 | 253 | -3 | -3 | -4 | -3 | -4 | -4 | -4 | -3 | -4 | -5 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -6 | -6 | -5 | -6 | -4 | -3 | -4 | -3
| 32.8 | 116 | 116 | 125 | 134 | 141 | 148 | 155 | 161 | 166 | 171 | 176 | 181 | 185 | 189 | 193 | 197 | 200 | 204 | 207 | 210 | 216 | 221 | 227 | 231 | 236 | 242 | 246 | 250 | -3 | -3 | -3 | -4 | -3 | -4 | -4 | -5 | -4 | -4 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -5 | -6 | -5 | -6 | -6 | 2 | -2 | -3 | -3
| 32.9 | 113 | 113 | 122 | 130 | 138 | 144 | 151 | 156 | 162 | 167 | 172 | 176 | 180 | 184 | 188 | 192 | 195 | 198 | 202 | 205 | 210 | 216 | 221 | 225 | 238 | 240 | 243 | 247 | -3 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -6 | -5 | -6 | -6 | -6 | -14 | -7 | -3 | -4
| 33 | 110 | 110 | 119 | 127 | 134 | 140 | 147 | 152 | 157 | 162 | 167 | 171 | 175 | 179 | 183 | 187 | 190 | 193 | 196 | 199 | 205 | 210 | 215 | 219 | 224 | 233 | 240 | 243 | -4 | -4 | -4 | -4 | -4 | -3 | -5 | -4 | -4 | -4 | -5 | -4 | -4 | -5 | -4 | -6 | -5 | -5 | -5 | -5 | -6 | -6 | -6 | -6 | -5 | -6 | -5 | -3
| 33.1 | 106 | 106 | 115 | 123 | 130 | 137 | 142 | 148 | 153 | 158 | 162 | 167 | 171 | 174 | 179 | 181 | 185 | 188 | 191 | 194 | 199 | 204 | 209 | 213 | 219 | 227 | 235 | 240 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -4 | -5 | -5 | -5 | -6 | -5 | -6 | -6 | -6 | -6 | -6 | -8 | -6 | -6 | -8 | -6 | -6 | -4
| 33.2 | 103 | 103 | 112 | 119 | 126 | 133 | 138 | 144 | 149 | 153 | 158 | 162 | 166 | 169 | 173 | 176 | 179 | 182 | 185 | 188 | 193 | 196 | 203 | 207 | 211 | 221 | 229 | 236 | -3 | -3 | -4 | -3 | -3 | -4 | -4 | -5 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -3 | -6 | -6 | -6 | -7 | -7 | -7
| 33.3 | 100 | 100 | 108 | 116 | 123 | 129 | 134 | 139 | 144 | 149 | 153 | 157 | 161 | 164 | 168 | 171 | 174 | 177 | 180 | 183 | 188 | 193 | 197 | 201 | 205 | 214 | 222 | 229 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -6 | -6 | -6 | -6 | -6 | -6 | -6 | -7 | -7
| 33.4 | 97 | 97 | 105 | 112 | 119 | 125 | 130 | 135 | 140 | 144 | 148 | 152 | 156 | 159 | 163 | 166 | 169 | 172 | 174 | 177 | 182 | 187 | 191 | 195 | 199 | 208 | 215 | 222 | -3 | -3 | -3 | -3 | -4 | -4 | -2 | -4 | -5 | -4 | -4 | -5 | -5 | -5 | -6 | -5 | -6 | -6 | -5 | -6 | -6 | -6 | -6 | -6 | -6 | -7 | -7 | -7
| 33.5 | 94 | 94 | 102 | 109 | 115 | 121 | 128 | 131 | 135 | 140 | 144 | 147 | 151 | 154 | 157 | 161 | 163 | 166 | 169 | 171 | 176 | 181 | 185 | 189 | 193 | 201 | 208 | 215 | -3 | -3 | -4 | -4 | -4 | -4 | -6 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -5 | -6 | -5 | -5 | -6 | -6 | -6 | -7 | -8 | -6 | -9
| 33.6 | 91 | 91 | 98 | 105 | 111 | 117 | 122 | 126 | 131 | 135 | 139 | 142 | 146 | 149 | 152 | 155 | 158 | 161 | 163 | 166 | 171 | 175 | 179 | 183 | 186 | 193 | 202 | 206 | -4 | -4 | -3 | -4 | -4 | -4 | -5 | -4 | -5 | -5 | -4 | -4 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -6 | -6 | -6 | -6 | -6 | -6 | -5 | -7 | -5
| 33.7 | 87 | 87 | 95 | 101 | 107 | 113 | 117 | 122 | 126 | 130 | 135 | 138 | 141 | 144 | 147 | 150 | 153 | 155 | 158 | 160 | 165 | 169 | 173 | 177 | 180 | 188 | 195 | 201 | -3 | -3 | -4 | -3 | -4 | -5 | -4 | -4 | -4 | -2 | -6 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -6 | -5 | -6 | -6 | -6 | -7 | -6 | -7 | -7 | -7
| 33.8 | 84 | 84 | 91 | 98 | 103 | 108 | 113 | 118 | 122 | 128 | 129 | 133 | 136 | 139 | 142 | 145 | 147 | 150 | 152 | 155 | 159 | 163 | 167 | 170 | 174 | 181 | 188 | 194 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -5 | -5 | -7 | -5 | -5 | -5 | -5 | -5 | -6 | -5 | -6 | -5 | -6 | -6 | -6 | -6 | -6 | -7 | -8 | -7 | -7
| 33.9 | 81 | 81 | 88 | 94 | 99 | 104 | 109 | 113 | 117 | 121 | 124 | 128 | 131 | 134 | 137 | 139 | 142 | 144 | 147 | 149 | 153 | 157 | 161 | 164 | 167 | 173 | 181 | 187 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -4 | -4 | -6 | -4 | -5 | -5 | -5 | -6 | -5 | -6 | -5 | -6 | -6 | -6 | -6 | -6 | -6 | -6 | -7 | -7 | -7
| 34 | 78 | 78 | 84 | 90 | 95 | 100 | 105 | 109 | 113 | 115 | 120 | 123 | 126 | 129 | 131 | 134 | 136 | 139 | 141 | 143 | 147 | 151 | 155 | 158 | 161 | 166 | 174 | 180 | -4 | -4 | -3 | -4 | -4 | -4 | -5 | -5 | -4 | -3 | -5 | -5 | -5 | -6 | -5 | -5 | -5 | -6 | -6 | -6 | -6 | -6 | -7 | -6 | -6 | -5 | -7 | -7
| 34.1 | 74 | 74 | 81 | 86 | 91 | 96 | 100 | 104 | 109 | 112 | 115 | 118 | 121 | 123 | 126 | 129 | 131 | 133 | 135 | 137 | 141 | 145 | 148 | 152 | 155 | 161 | 167 | 173 | -3 | -3 | -4 | -3 | -3 | -4 | -4 | -4 | -6 | -5 | -5 | -5 | -3 | -5 | -5 | -6 | -6 | -5 | -5 | -5 | -6 | -6 | -6 | -7 | -7 | -6 | -7 | -7
| 34.2 | 71 | 71 | 77 | 83 | 88 | 92 | 96 | 100 | 103 | 107 | 110 | 113 | 118 | 118 | 121 | 123 | 125 | 128 | 130 | 132 | 135 | 139 | 142 | 145 | 148 | 155 | 160 | 166 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -5 | -4 | -5 | -5 | -5 | -8 | -5 | -6 | -5 | -5 | -6 | -6 | -6 | -5 | -6 | -6 | -6 | -6 | -9 | -7 | -8
| 34.3 | 68 | 68 | 74 | 79 | 84 | 88 | 92 | 95 | 99 | 102 | 105 | 108 | 110 | 113 | 115 | 118 | 120 | 122 | 124 | 126 | 130 | 133 | 136 | 139 | 142 | 146 | 153 | 158 | -4 | -4 | -4 | -4 | -4 | -4 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -6 | -6 | -6 | -6 | -6 | -6 | -6 | -6 | -7 | -5 | -7 | -7
| 34.4 | 64 | 64 | 70 | 75 | 80 | 84 | 87 | 91 | 94 | 97 | 100 | 103 | 105 | 108 | 110 | 112 | 114 | 116 | 118 | 120 | 124 | 127 | 130 | 133 | 135 | 141 | 146 | 151 | -3 | -3 | -3 | -4 | -2 | -5 | -4 | -5 | -4 | -5 | -5 | -5 | -5 | -6 | -5 | -5 | -5 | -5 | -6 | -6 | -6 | -6 | -7 | -7 | -6 | -7 | -7 | -7
| 34.5 | 61 | 61 | 67 | 71 | 78 | 79 | 83 | 86 | 90 | 92 | 95 | 98 | 100 | 102 | 105 | 107 | 109 | 111 | 112 | 114 | 118 | 121 | 123 | 126 | 129 | 134 | 139 | 144 | -3 | -3 | -4 | -4 | -6 | -4 | -4 | -4 | -5 | -4 | -5 | -5 | -5 | -5 | -6 | -6 | -6 | -6 | -5 | -8 | -6 | -7 | -6 | -6 | -7 | -6 | -7 | -7
| 34.6 | 58 | 58 | 63 | 67 | 72 | 75 | 79 | 82 | 85 | 88 | 90 | 93 | 95 | 97 | 99 | 101 | 103 | 105 | 107 | 106 | 112 | 114 | 117 | 120 | 122 | 128 | 132 | 137 | -4 | -4 | -4 | -3 | -5 | -4 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -6 | -6 | -4 | -7 | -6 | -6 | -7 | -6 | -7 | -7 | -8
| 34.7 | 54 | 54 | 59 | 64 | 67 | 71 | 74 | 77 | 80 | 83 | 85 | 88 | 90 | 92 | 94 | 96 | 98 | 99 | 101 | 102 | 105 | 108 | 111 | 113 | 116 | 121 | 125 | 129 | -3 | -3 | -3 | -4 | -4 | -4 | -4 | -4 | -5 | -5 | -5 | -6 | -6 | -4 | -6 | -6 | -6 | -6 | -6 | -5 | -6 | -6 | -7 | -6 | -7 | -7 | -7 | -7
| 34.8 | 51 | 51 | 56 | 60 | 63 | 67 | 70 | 73 | 75 | 78 | 80 | 82 | 84 | 88 | 88 | 90 | 92 | 93 | 95 | 97 | 99 | 102 | 104 | 107 | 109 | 114 | 118 | 122 | -3 | -3 | -4 | -4 | -4 | -4 | -5 | -5 | -4 | -5 | -5 | -5 | -6 | -7 | -5 | -5 | -6 | -5 | -6 | -6 | -6 | -6 | -6 | -7 | -7 | -7 | -7 | -7
| 34.9 | 48 | 48 | 52 | 56 | 59 | 63 | 65 | 68 | 71 | 73 | 75 | 77 | 78 | 81 | 83 | 85 | 86 | 88 | 89 | 91 | 93 | 96 | 98 | 100 | 102 | 107 | 111 | 115 | -48 | -48 | -52 | -56 | -59 | -63 | -65 | -68 | -71 | -73 | -75 | -77 | -78 | -81 | -83 | -85 | -86 | -88 | -89 | -91 | -93 | -96 | -98 | -100 | -102 | -107 | -111 | -115

## Unit Conversion
Back to INDEX
Length |  |  |  |  | Power |  |  |  | Dynamic Viscosity |  |  | Heat Flux
|  | 8 | 0.4 |  |  |  | 1 | 197 |  | 5 | 1 |  | 1 | 1 | [6 empty] | 304.8 | 0.0013123 |  |  |  | 28.3168 | 4.326 |  |  |  | 1 | 1 |  |  |  | 60 | 3.8133 |  |  |  | 1900-01-05 21:28 | 0.72519 |  |  |  | 1899-12-31 | 1900-07-15 |  |  |  | 1899-12-31 | 2064-04-08 |  |  |  | 1899-12-31 | 1900-05-09 |  |  |  | 0.092903 | 2076-10-25 11:06 |  |  |  | 1899-12-31 | 1900-03-02 09:36 |  |  |  | 0.00067197 | 1904-01-27 03:56 |  |  |  | 0.36 | 1900-01-01 18:40 |  |  |  | 0.000126 | 1921-09-22 15:22 |  |  |  | 1899-12-31 | 1960-03-25 |  |  |  | 1899-12-31 | 1899-12-31 |  |  |  | 1899-12-31 | 1899-12-31 |  |  |  | 1899-12-31 | 1899-12-31 |  |  |  | 1899-12-31 | 1899-12-31
|  | 6 | 0.0004 |  |  |  | 6 | 146.9029 |  | 9 | 5357.39 |  | 5 | 3.1546 |  |  |  | 1 | mile | 0.00018939 | 2.4855e-07 |  | 1 | yard 3 | 0.037037 | 0.16022 |  | 1 | MMscf / hr | 0.00037867 | 0.00037867 |  | 1 | ft 3 / sec | 1 | 3.8133 |  | 1899-12-31 | psi | 1 | 0.72519 |  | 1899-12-31 | hp | 1 | 1900-07-15 |  | 1899-12-31 | hp . hr | 0.00039301 | 1900-01-22 13:56 |  | 1899-12-31 | Long Ton | 0.00098421 | 0.12795 |  | 1899-12-31 | ft2 | 1 | 2076-10-25 11:06 |  | 1899-12-31 | gr / cm3 | 0.016018 | 0.99955 |  | 1899-12-31 | centipoise | 1899-12-31 | 1904-01-27 03:56 |  | 1899-12-31 | centistoke | 1900-04-09 | 1900-10-03 18:40 |  | 1899-12-31 | lb / sec | 0.00027778 | 1900-01-01 04:55 |  | 1899-12-31 | Btu / hr . ft2 . F | 1 | 1960-03-25 |  | 1899-12-31 | Btu / hr . ft . F | 1 | 1899-12-31 |  | 1899-12-31 | Btu / hr . ft2 | 1 | 1899-12-31 |  | 1899-12-31 | Btu / lb | 1 | 1899-12-31 |  | 1899-12-31 | Btu / lb . F | 1 | 1899-12-31
[18 empty] | 2 | yard | 0.33333 | 0.00043745 |  | 2 | bbl | 0.17811 | 0.7705 |  | 2 | MMscf / day | 0.009088 | 0.009088 |  | 2 | ft 3 / min | 60 | 228.8 |  | 1900-01-01 | in Hg | 2.0418 | 1899-12-31 11:32 |  | 1900-01-01 | hp (metric) | 1899-12-31 00:20 | 1900-07-17 17:43 |  | 1900-01-01 | Btu | 1899-12-31 | 2064-04-08 |  | 1900-01-01 | Short Ton | 0.0011023 | 0.1433 |  | 1900-01-01 | in2 | 144 | 9300018.6 |  | 1900-01-01 | gr / ml | 0.016018 | 0.99955 |  | 1900-01-01 | poise | 0.01 | 1900-01-13 21:10 |  | 1900-01-01 | stoke | 1899-12-31 | 1900-01-01 18:40 |  | 1900-01-01 | lb / min | 0.016667 | 1900-05-11 06:39 |  | 1900-01-01 | cal / sec . cm2 . C | 0.00013562 | 1900-01-01 23:37 |  | 1900-01-01 | cal / sec . cm . C | 0.0041338 | 0.0041338 |  | 1900-01-01 | cal / sec . cm2 | 7.5346e-05 | 7.5346e-05 |  | 1900-01-01 | cal / gr | 0.55556 | 0.55556 |  | 1900-01-01 | cal / gr . C | 1 | 1899-12-31
Volume |  |  |  |  | Energy |  |  |  | Kinematic Viscosity |  |  | Specific Energy | [5 empty] | 3 | ft | 1 | 0.0013123 |  | 3 | ft 3 | 1 | 4.326 |  | 3 | Mscf / hr | 0.37867 | 0.37867 |  | 3 | ft 3 / hr | 3600 | 13728 |  | 1900-01-02 | mm Hg | 1900-02-19 17:10 | 1900-02-05 12:05 |  | 1900-01-02 | ton (refrig.) | 0.21204 | 1900-02-09 18:31 |  | 1900-01-02 | ft . lbf | 778.1693 | 46690158 |  | 1900-01-02 | Metric Ton | 0.001 | 0.13 |  | 1900-01-02 | yard 2 | 0.11111 | 1919-08-23 22:33 |  | 1900-01-02 | gr / lit | 16.0185 | 1902-09-25 13:15 |  | 1900-01-02 | Pa . sec | 0.001 | 1899-12-31 11:43 |  | 1900-01-02 | ft2 / sec | 0.0010764 | 0.00299 |  | 1900-01-02 | lb / hr | 1899-12-31 | 1921-09-22 15:22 |  | 1900-01-02 | watt / cm2 . C | 0.00056783 | 1900-01-11 11:49 |  | 1900-01-02 | watt / cm . C | 0.017307 | 0.017307 |  | 1900-01-02 | watt / cm2 | 0.00031546 | 0.00031546 |  | 1900-01-02 | joule / gr | 2.326 | 1900-01-01 07:49 |  | 1900-01-02 | joule / gr . C | 4.1868 | 1900-01-03 04:29
|  | 9 | 122.5 |  |  |  | 2 | 60000 |  | 6 | 1 |  | 1 | 1 |  |  |  | 4 | in | 12 | 0.015748 |  | 4 | gal (Imperial) | 6.2288 | 26.9462 |  | 4 | Mscf / day | 9.088 | 9.088 |  | 4 | bbl / hr | 641.1874 | 2445.0613 |  | 1900-01-03 | ft H2O | 1900-01-01 07:25 | 1899-12-31 16:11 |  | 1900-01-03 | Btu / min | 1900-02-10 09:22 | 1922-11-10 22:31 |  | 1900-01-03 | kW . hr | 0.00029307 | 1900-01-16 14:01 |  | 1900-01-03 | lb | 2.2046 | 1900-10-12 14:21 |  | 1900-01-03 | mile 2 | 3.587e-08 | 0.0023166 |  | 1900-01-03 | gr / gal | 60.6365 | 1910-05-10 17:09 |  | 1900-01-03 | lb / ft . hr | 1900-01-01 10:03 | 1909-11-07 23:59 |  | 1900-01-03 | ft2 / hr | 1900-01-02 21:00 | 1900-01-09 18:20 |  | 1900-01-03 | lb / day | 1900-01-23 | 2421-07-05 08:46 |  | 1900-01-03 | kcal / hr . m2 . C | 1900-01-03 21:11 | 2194-01-30 09:59 |  | 1900-01-03 | kcal / hr . m . C | 1899-12-31 11:43 | 1899-12-31 11:43 |  | 1900-01-03 | kcal / hr . m2 | 1900-01-01 17:06 | 1900-01-01 17:06 |  | 1900-01-03 | cal / kg | 1901-07-08 13:20 | 1901-07-08 13:20 |  | 1900-01-03 | cal / kg . C | 1902-09-26 | 1902-09-26
|  | 11 | 122500 |  |  |  | 4 | 17.5843 |  | 5 | 0.00027778 |  | 5 | 2326 |  |  |  | 5 | km | 0.0003048 | 4e-07 |  | 5 | gal (US) | 7.4805 | 32.3611 |  | 5 | lb-mol / hr | 1 | 1 |  | 5 | bbl / day | 15388.5 | 58681.48 |  | 1900-01-04 | in H2O | 27.7076 | 1900-01-19 02:14 |  | 1900-01-04 | Btu / hr | 1906-12-18 10:24 | 501253.301 |  | 1900-01-04 | Cal | 1900-09-08 03:57 | 15129864 |  | 1900-01-04 | oz | 1900-02-03 06:35 | 1912-07-20 14:53 |  | 1900-01-04 | mm2 | 2154-05-10 00:58 | 6000000000 |  | 1900-01-04 | kg / m3 | 1900-01-15 00:27 | 1902-09-25 13:15 |  | 1900-01-04 | lb / ft . sec | 0.00067197 | 1899-12-31 |  | 1900-01-04 | m2 / sec | 0.0001 | 0.00027778 |  | 1900-01-04 | kg / sec | 0.000126 | 1899-12-31 |  | 1900-01-04 | watt / m2 . C | 5.6783 | 2242-01-07 19:24 |  | 1900-01-04 | watt / m . C | 1.7307 | 1899-12-31 17:32 |  | 1900-01-04 | watt / m2 | 3.1546 | 1900-01-02 03:43 |  | 1900-01-04 | joule / kg | 2326 | 1906-05-14 |  | 1900-01-04 | joule / kg . C | 4186.8 | 1911-06-17 19:12
[18 empty] | 6 | m | 0.3048 | 0.0004 |  | 6 | fl. oz | 957.5065 | 4142.2173 |  | 6 | lb-mol / day | 24 | 24 |  | 6 | gal / min | 448.8312 | 1711.543 |  | 1900-01-05 | torr | 1900-02-19 17:10 | 1900-02-05 12:05 |  | 1900-01-05 | kW | 0.7457 | 1900-05-25 21:40 |  | 1900-01-05 | kCal | 0.25216 | 1941-06-02 20:44 |  | 1900-01-05 | kg | 1899-12-31 | 1900-05-09 |  | 1900-01-05 | cm2 | 1902-07-17 00:44 | 60000000 |  | 1900-01-05 | lb / in3 | 0.0005787 | 0.036111 |  | 1900-01-05 | lbf . sec / ft2 | 2.0885e-05 | 0.031081 |  | 1900-01-05 | m2 / hr | 0.36 | 1 |  | 1900-01-05 | kg / min | 0.0075599 | 1900-02-28
Molar Flowrate |  |  |  |  | Mass |  |  |  | Mass Flowrate |  |  | Specific Heat | [5 empty] | 7 | cm | 30.48 | 0.04 |  | 7 | in 3 | 1728 | 7475.4078 |  | 7 | g-mol / hr | 453.5924 | 453.5924 |  | 7 | gal / day | 646316.9 | 2464621.7787 |  | 1900-01-06 | atm | 0.068046 | 0.049346 |  | 1900-01-06 | Cal / sec | 178.23 | 1996-02-16 07:26 |  | 1900-01-06 | joule | 1055.056 | 63303360 |  | 1900-01-06 | gr | 1000 | 2255-12-04 |  | 1900-01-06 | m2 | 0.092903 | 1916-06-04 |  | 1900-01-06 | lb / ft3 | 1 | 1900-03-02 09:36 |  | 1900-01-06 | lbf . sec / in2 | 1.4504e-07 | 0.00021584 |  | 1900-01-06 | cm2 / sec | 1 | 1900-01-01 18:40 |  | 1900-01-06 | kg / hr | 0.45359 | 1909-11-08
|  | 5 | 1 |  |  |  | 6 | 130 |  | 5 | 1 |  | 1 | 1 |  |  |  | 8 | mm | 304.8 | 0.4 |  | 8 | m 3 | 0.028317 | 0.1225 |  | 8 | g-mol / day | 10886.22 | 10886.22 |  | 8 | m 3 / sec | 0.028317 | 0.10798 |  | 1900-01-07 | bar | 0.068948 | 0.05 |  | 1900-01-07 | Cal / min | 1929-04-10 19:12 | 2106678.6 |  | 1900-01-07 | W . sec | 1902-11-20 01:21 | 63303360 |  | 1900-01-07 | mg | 1000000 | 130000000 |  | 1900-01-07 | km2 | 9.2903e-08 | 0.006 |  | 1900-01-07 | lb / gal | 0.13368 | 1900-01-07 08:12 |  | 1900-01-07 | gr / cm . sec | 1899-12-31 | 1904-01-27 03:56 | [6 empty] | 1900-01-07 | kg / day | 1900-01-09 21:16 | 2136-07-19 23:49
|  | 3 | 0.37867 |  |  |  | 4 | 286.598 |  | 6 | 60 |  | 5 | 4186.8 |  |  |  | 9 | micron | 304800 | 400 |  | 9 | lit | 28.3168 | 122.5 | [6 empty] | 9 | m 3 / min | 1.699 | 6.4789 |  | 1900-01-08 | mbar | 68.9476 | 1900-02-18 |  | 1900-01-08 | Watt | 745.6999 | 2302-03-15 21:08 |  | 1900-01-08 | ft3 . lbf / in2 | 5.4039 | 324234 |  | 1900-01-08 | grain | 15432 | 2006160 |  | 1900-01-08 | hectare | 9.2903e-06 | 0.6 |  | 1900-01-08 | lb / bbl | 5.6146 | 1900-12-15 08:24 |  | 1900-01-08 | kg / m . hr | 1900-01-02 14:24 | 1914-08-31 09:22 | [6 empty] | 1900-01-08 | L ton / day | 0.010714 | 1900-03-25 00:51
[23 empty] | 10 | cm 3 | 28316.85 | 122500 | [6 empty] | 10 | m 3 / hr | 101.9407 | 388.7339 |  | 1900-01-09 | kg / cm2 | 0.070307 | 0.050986 |  | 1900-01-09 | Joule / sec | 745.7 | 2302-03-15 21:36 |  | 1900-01-09 | lit . atm | 10.412 | 624720 |  | 1900-01-09 | carat | 5000 | 650000 |  | 1900-01-09 | are | 0.00092903 | 1900-02-28 |  | 1900-01-09 | oz / in3 | 0.0092593 | 0.57778 | [11 empty] | 1900-01-09 | S ton / day | 0.012 | 1900-04-04 05:45
Volumetric Flowrate |  |  |  |  | Density |  |  |  | Heat Transfer Coefficient |  |  | Temperature | [10 empty] | 11 | ml | 28316.85 | 122500 | [6 empty] | 11 | lit / sec | 28.3168 | 107.9816 |  | 1900-01-10 | kPa | 6.8948 | 1900-01-04 |  | 1900-01-10 | ft . lbf / sec | 550 | 2196-08-24 | [6 empty] | 1900-01-10 | slug | 0.068522 | 1900-01-07 21:47 |  | 1900-01-10 | acre | 2.2957e-05 | 1899-12-31 11:35 |  | 1900-01-10 | oz / gal | 2.1389 | 1900-05-12 11:12 | [11 empty] | 1900-01-10 | M ton / day | 0.010886 | 1900-03-26 09:36
|  | 2 | 228.8 |  |  |  | 7 | 62.4 |  | 1 | 22000 | °C | 1 | 32 | °C | 88.6 | [16 empty] | 12 | lit / min | 1699.011 | 6478.8953 |  | 1900-01-11 | Pa | 6894.757 | 1913-09-08 |  | 1900-01-11 | ft . lbf / min | 33000 | 6501000 | [16 empty] | 1900-01-11 | SG (liquid) | 0.016018 | 0.99955
|  | 8 | 0.10798 |  |  |  | 12 | 0.99955 |  | 5 | 124921.808 | °Farenheit | 5 | 450 | °Farenheit | 232.2222 | [16 empty] | 13 | lit / hr | 101940.7 | 388733.8693
[12 empty] | °C | 1 | 232.2222 | [18 empty] | 14 | lit / day | 2446576.8 | 9329612.864
Pressure |  |  |  |  | Area |  |  |  | Thermal Conductivity |  |  | °Farenheit | 5 | 88.6
|  | 11 | 5 |  |  |  | 7 | 6000 |  | 1 | 1
|  | 10 | 0.050986 |  |  |  | 1 | 64583.4625 |  | 3 | 0.017307 | [5 empty] | 510
Feet per second to meters per second |  |  | 50 | fps |  | 7800 | fps | CFM
|  |  | 15.2393 | m/s |  | 3.6816 | m/s | m³/s
How to convert BTU/hr to kW
1 BTU/hr = | 0.00029307 |  |  | kW
kW | 2.5 | Input
BTU | 8530.3541
BTU | 32000 | Input
kWh | 9.3783 | W/m²
kW | 9.3783 | W/m131 | The power P in kilowatts (kW) is equal to the energy E in kilowatt-hour (kWh), divided by the time period t in hours (hr):
W | 9378.2742 |  | P(kW) = E(kWh) / t(hr)
| 18756.5485 |  | So kilowatt = kilowatt-hour / hour
or kW = kWh / h
Dilution Product % | 35% |  | %
Final Mixture % | 3% |  | %
Dilution Product Volume | 50 |  | ml
Add 0% Volume to get Final Mixture % | 583.3333 |  | ml

## Vehicle Qty & heat graph
| Vehicle kW Minimum Qty Calculator |  |  |  | Back to INDEX
Yes = 1 No = 0
| Development end | 1 | 0.4 | kW/m
| Loading end | 0 | 0.5 | kW/m
|  |  | 0.9 | kW/m
| Vent Column Increment increase - m | 50 | m
| Reject Temperature (Max) | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | °C
| Reject Temperature (Design) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | °C
| Return Wet Bulb | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | °C
| Return Dry Bulb | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | °C
| BP | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | Kpa
| Vapour Press (Pw) | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | 3.0482 | Kpa
| Moisture Content ( r ) | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | 0.017165 | g/Kg
| Moisture Content ( g/Kg ) | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | 17.1655 | g/Kg
| Specific Volume ( v ) | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | 0.8033 | m³/Kg
| Density ( w ) | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | 1.2662 | Kg/m³
| Enthalpy ( H ) | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | 80.2232 | Kj/Kg
| Sigma Heat ( S ) | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | 78.2501 | Kj/Kg
| Relative Humidity | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | 51.3326 | %
| Dewpoint Temperature ( tdp ) | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | 15.3417 | °C
Intake Temperature
| Intake Wet Bulb | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | °C
| Intake Dry Bulb | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | °C
| BP | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | 113.5 | Kpa
| Vapour Press (Pw) | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | 2.2964 | Kpa
| Moisture Content ( r ) | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | 0.012845 | g/Kg
| Moisture Content ( g/Kg ) | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | 12.8446 | g/Kg
| Specific Volume ( v ) | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | 0.78239 | m³/Kg
| Density ( w ) | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | 1.2946 | Kg/m³
| Enthalpy ( H ) | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | 62.9678 | Kj/Kg
| Sigma Heat ( S ) | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | 61.733 | Kj/Kg
| Relative Humidity | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | 54.1478 | %
| Dewpoint Temperature ( tdp ) | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | 12.4974 | °C
| Development End Heatload /m | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | kW/m
| Loading End Heatload /m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kW/m
| End Length | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | m
| End Heatload - Development | 20 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | 180 | 200 | 220 | 240 | 260 | 280 | 300 | 320 | kW
| End Heatload Loading XC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kW
| Q = Vehicle kW | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | 256 | kW
| Heatload Factor | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Fan kW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | kW
| Vehicle Heatload | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | 384 | kW
| Total Heatload | 459 | 479 | 499 | 519 | 539 | 559 | 579 | 599 | 619 | 639 | 659 | 679 | 699 | 719 | 739 | 759 | kW
| Qty Dilution Requirement | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | m³/s
| Qty Required (kW x Dilution Requirement) | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | 15.36 | m³/s
| Leakage % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | /100m
| Expected Leakage over distance "Total Leakage" | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | %
| Massflow in end | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | kg/s
| kg/s Airflow Required | 27.7894 | 29.0003 | 30.2111 | 31.422 | 32.6329 | 33.8437 | 35.0546 | 36.2655 | 37.4763 | 38.6872 | 39.8981 | 41.1089 | 42.3198 | 43.5307 | 44.7415 | 45.9524 | kg/s
| Discharge Qty Required | 21.4663 | 22.4016 | 23.337 | 24.2723 | 25.2077 | 26.143 | 27.0784 | 28.0137 | 28.9491 | 29.8844 | 30.8198 | 31.7551 | 32.6905 | 33.6258 | 34.5612 | 35.4965 | m³/s
| Fan Intake Qty Required | 22.5396 | 24.6418 | 26.8375 | 29.1268 | 31.5096 | 33.9859 | 36.5558 | 39.2192 | 41.9762 | 44.8266 | 47.7707 | 50.8082 | 53.9393 | 57.1639 | 60.4821 | 63.8938 | m³/s
| Expected Reject temperature | 19.9565 | 20.8261 | 21.6957 | 22.5652 | 23.4348 | 24.3043 | 25.1739 | 26.0435 | 26.913 | 27.7826 | 28.6522 | 29.5217 | 30.3913 | 31.2609 | 32.1304 | 33 | °C
| Wet Bulb / Dry Bulb Gap | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Minimum Massflow to Achieve Reject | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844 | 19.8844
| Sigma Heat ( S ) Air Out | 84.8163 | 85.8221 | 86.828 | 87.8338 | 88.8396 | 89.8454 | 90.8512 | 91.857 | 92.8628 | 93.8686 | 94.8744 | 95.8803 | 96.8861 | 97.8919 | 98.8977 | 99.9035 | kW/m
| Formula : q = M x ΔS | Qty = q / ΔS / w
| Airflow Required for different Vehicles to achieve 27.5°CWB if intake temperature is °CWB |  |  |  |  | 23 | 30 | dilution Qty = | 0.06 | Heat Factor= | 1.5 | different end lengths
220 | 220kW Vehicle | 18.9408 | 19.8762 | 20.8115 | 21.7469 | 22.6822 | 23.6176 | 24.5529 | 25.4883 | 26.4236 | 27.359 | 28.2943 | 29.2297 | 30.165 | 31.1004 | 32.0357 | 32.9711 | m³/s
250 | 250kW Vehicle | 21.0454 | 21.9807 | 22.9161 | 23.8514 | 24.7868 | 25.7221 | 26.6575 | 27.5928 | 28.5282 | 29.4635 | 30.3989 | 31.3342 | 32.2696 | 33.2049 | 34.1403 | 35.0756 | m³/s
280 | 280kW Vehicle | 23.1499 | 24.0853 | 25.0206 | 25.956 | 26.8913 | 27.8267 | 28.762 | 29.6974 | 30.6327 | 31.5681 | 32.5034 | 33.4388 | 34.3741 | 35.3095 | 36.2448 | 37.1802 | m³/s
300 | 300kW Vehicle | 24.5529 | 25.4883 | 26.4236 | 27.359 | 28.2943 | 29.2297 | 30.165 | 31.1004 | 32.0357 | 32.9711 | 33.9064 | 34.8418 | 35.7771 | 36.7125 | 37.6478 | 38.5832 | m³/s
330 | 330kW Vehicle | 26.6575 | 27.5928 | 28.5282 | 29.4635 | 30.3989 | 31.3342 | 32.2696 | 33.2049 | 34.1403 | 35.0756 | 36.011 | 36.9463 | 37.8817 | 38.817 | 39.7524 | 40.6877 | m³/s
350 | 350kW Vehicle | 28.0605 | 28.9958 | 29.9312 | 30.8665 | 31.8019 | 32.7372 | 33.6726 | 34.6079 | 35.5433 | 36.4786 | 37.414 | 38.3493 | 39.2847 | 40.22 | 41.1554 | 42.0907 | m³/s
375 | 375kW Vehicle | 29.8143 | 30.7496 | 31.685 | 32.6203 | 33.5557 | 34.491 | 35.4264 | 36.3617 | 37.2971 | 38.2324 | 39.1678 | 40.1031 | 41.0385 | 41.9738 | 42.9092 | 43.8445 | m³/s
| Expected End Reject Temps for different Vehicles | If intake temperature = |  | 23 | 30 | dilution Qty = | 0.06 | Heat Factor= | 1.5 | different end lengths
220 | 220kW Vehicle | 75.5872 | 75.0087 | 74.4766 | 73.9855 | 73.5309 | 73.1088 | 72.7158 | 72.3491 | 72.0061 | 71.6846 | 71.3826 | 71.0983 | 70.8304 | 70.5773 | 70.3379 | 70.1112 | °C
250 | 250kW Vehicle | 77.2065 | 76.5604 | 75.9661 | 75.4176 | 74.9099 | 74.4384 | 73.9995 | 73.59 | 73.2069 | 72.8478 | 72.5104 | 72.193 | 71.8937 | 71.6111 | 71.3437 | 71.0905 | °C
280 | 280kW Vehicle | 78.8258 | 78.1121 | 77.4556 | 76.8498 | 76.2888 | 75.7681 | 75.2833 | 74.8308 | 74.4076 | 74.0109 | 73.6383 | 73.2876 | 72.957 | 72.6448 | 72.3495 | 72.0697 | °C
300 | 300kW Vehicle | 79.9054 | 79.1466 | 78.4487 | 77.8045 | 77.2082 | 76.6545 | 76.1391 | 75.6581 | 75.2081 | 74.7864 | 74.3902 | 74.0174 | 73.6659 | 73.334 | 73.02 | 72.7226 | °C
330 | 330kW Vehicle | 81.5247 | 80.6983 | 79.9382 | 79.2366 | 78.5871 | 77.9841 | 77.4228 | 76.8989 | 76.4089 | 75.9496 | 75.5181 | 75.1121 | 74.7292 | 74.3677 | 74.0258 | 73.7019 | °C
350 | 350kW Vehicle | 82.6042 | 81.7328 | 80.9312 | 80.1914 | 79.5065 | 78.8706 | 78.2786 | 77.7261 | 77.2094 | 76.725 | 76.27 | 75.8418 | 75.4381 | 75.0569 | 74.6963 | 74.3547 | °C
375 | 375kW Vehicle | 83.9537 | 83.0259 | 82.1725 | 81.3848 | 80.6556 | 79.9786 | 79.3483 | 78.7602 | 78.21 | 77.6943 | 77.2099 | 76.754 | 76.3242 | 75.9184 | 75.5345 | 75.1708 | °C
| End Length | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | m
| Vuma End Face Temps for different Vehicles at 23°CWB Intake (If Qty does not change) | If intake temperature = |  | 23 | 30 | dilution Qty = | 0.06 | Heat Factor= | 1.5 | different end lengths | [8 empty] | Quantity used
220 | 220kW Vehicle (330kW) | 27.5 | 27.74 | 27.98 | 28.22 | 28.46 | 28.7 | 28.925 | 29.15 | 29.375 | 29.6 | 29.8 | 30 | 30.2 | 30.4 | 30.6 | 30.8 | °C | 18.9408 | m³/s
250 | 250kW Vehicle (375kW) | 27.5 | 27.72 | 27.94 | 28.16 | 28.38 | 28.6 | 28.8 | 29 | 29.2 | 29.4 | 29.6 | 29.8 | 30 | 30.2 | 30.4 | 30.6 | °C | 21.0454 | m³/s
280 | 280kW Vehicle (420kW) | 27.5 | 27.72 | 27.94 | 28.16 | 28.38 | 28.6 | 28.775 | 28.95 | 29.125 | 29.3 | 29.4667 | 29.6333 | 29.8 | 29.9667 | 30.1333 | 30.3 | °C | 23.1499 | m³/s
300 | 300kW Vehicle (450kW) | 27.5 | 27.7 | 27.9 | 28.1 | 28.3 | 28.5 | 28.675 | 28.85 | 29.025 | 29.2 | 29.3667 | 29.5333 | 29.7 | 29.8667 | 30.0333 | 30.2 | °C | 24.5529 | m³/s
330 | 330kW Vehicle (495kW) | 27.5 | 27.68 | 27.86 | 28.04 | 28.22 | 28.4 | 28.55 | 28.7 | 28.85 | 29 | 29.1667 | 29.3333 | 29.5 | 29.6667 | 29.8333 | 30 | °C | 26.6575 | m³/s
350 | 350kW Vehicle (525kW) | 27.5 | 27.66 | 27.82 | 27.98 | 28.14 | 28.3 | 28.475 | 28.65 | 28.825 | 29 | 29.15 | 29.3 | 29.45 | 29.6 | 29.75 | 29.9 | °C | 28.0605 | m³/s
375 | 375kW Vehicle (563kW) | 27.5 | 27.66 | 27.82 | 27.98 | 28.14 | 28.3 | 28.45 | 28.6 | 28.75 | 28.9 | 29.0333 | 29.1667 | 29.3 | 29.4333 | 29.5667 | 29.7 | °C | 29.8143 | m³/s
Bold = actual VumA3D data
Interpolated data
| Expected End Reject Temps for different Vehicles | If intake temperature = |  | 23 | 30 | dilution Qty = | 0.06 | Heat Factor= | 1.5 | different end lengths
220 | 220kW Vehicle | 64.6125 | 72.6745 | 80.0903 | 86.9345 | 93.2708 | 99.1537 | 104.6302 | 109.7409 | 114.5214 | 119.0027 | 123.212 | 127.1733 | 130.9079 | 134.4347 | 137.7706 | 140.9308 | °C
250 | 250kW Vehicle | 42.0441 | 51.0484 | 59.331 | 66.9751 | 74.052 | 80.6226 | 86.7391 | 92.4473 | 97.7865 | 102.7916 | 107.4928 | 111.9171 | 116.0883 | 120.0273 | 123.7532 | 127.2827 | °C
280 | 280kW Vehicle | 19.4757 | 29.4223 | 38.5716 | 47.0158 | 54.8333 | 62.0914 | 68.8481 | 75.1536 | 81.0517 | 86.5805 | 91.7737 | 96.661 | 101.2687 | 105.62 | 109.7357 | 113.6346 | °C
300 | 300kW Vehicle | 4.4301 | 79.1466 | 78.4487 | 77.8045 | 77.2082 | 76.6545 | 76.1391 | 75.6581 | 75.2081 | 74.7864 | 74.3902 | 74.0174 | 73.6659 | 73.334 | 73.02 | 72.7226 | °C
330 | 330kW Vehicle | -18.1383 | 80.6983 | 79.9382 | 79.2366 | 78.5871 | 77.9841 | 77.4228 | 76.8989 | 76.4089 | 75.9496 | 75.5181 | 75.1121 | 74.7292 | 74.3677 | 74.0258 | 73.7019 | °C
350 | 350kW Vehicle | -33.1839 | 81.7328 | 80.9312 | 80.1914 | 79.5065 | 78.8706 | 78.2786 | 77.7261 | 77.2094 | 76.725 | 76.27 | 75.8418 | 75.4381 | 75.0569 | 74.6963 | 74.3547 | °C
375 | 375kW Vehicle | -51.9909 | 83.0259 | 82.1725 | 81.3848 | 80.6556 | 79.9786 | 79.3483 | 78.7602 | 78.21 | 77.6943 | 77.2099 | 76.754 | 76.3242 | 75.9184 | 75.5345 | 75.1708 | °C
(C70-C$20)/(-C$16*4.18)
(C71-C$20)/(-C$16*4.18)
|  | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | m
| Vuma End Face Temps for different Vehicles at 23°CWB Intake | If intake temperature = |  | 20 | 26 | dilution Qty = | 0.06 | Heat Factor= | 1.5 | different end lengths
220 | 220kW Vehicle (330kW) | 25.1 | 25.3 | 25.6 | 25.8 | 26.1 | 26.3 | 26.5 | 26.8 | 27 | 27.2 | 27.4 | 27.6 | 27.8 | 28 | 28.2 | 28.4 | °C
250 | 250kW Vehicle (375kW) | 25.5 | 25.8 | 26 | 26.3 | 26.5 | 26.8 | 27 | 27.2 | 27.4 | 27.6 | 27.8 | 28 | 28.2 | 28.4 | 28.6 | 28.8 | °C
280 | 280kW Vehicle (420kW) | 26 | 26.3 | 26.5 | 26.7 | 27 | 27.2 | 27.4 | 27.6 | 27.8 | 28 | 28.2 | 28.4 | 28.6 | 28.8 | 29 | 29.2 | °C
300 | 300kW Vehicle (450kW) | 26.3 | 26.6 | 26.8 | 27 | 27.3 | 27.5 | 27.7 | 27.9 | 28.1 | 28.3 | 28.5 | 28.7 | 28.9 | 29 | 29.2 | 29.4 | °C
330 | 330kW Vehicle (495kW) | 26.8 | 27 | 27.2 | 27.5 | 27.7 | 27.9 | 28.1 | 28.3 | 28.5 | 28.7 | 28.9 | 29.1 | 29.3 | 29.4 | 29.6 | 29.8 | °C
350 | 350kW Vehicle (525kW) | 27.1 | 27.3 | 27.5 | 27.8 | 28 | 28.2 | 28.4 | 28.6 | 28.8 | 29 | 29.2 | 29.3 | 29.5 | 29.7 | 29.8 | 30 | °C
375 | 375kW Vehicle (563kW) | 27.4 | 27.7 | 27.8 | 28.1 | 28.3 | 28.5 | 28.7 | 28.9 | 29.1 | 29.3 | 29.5 | 29.6 | 29.8 | 30 | 30.1 | 30.3 | °C
Note on C64: Johan van Sittert: Checked 100% in VumA3D
Note on T82: Johan van Sittert: Calculated Qty to achieve 27.5°C WB if intake Temp is 23.0°C WB

## T-less Veh + Qtys
Back to INDEX
Trackless Vehicle Data | [16 empty] | Air Volume / Diesel Dilution Table
Trackless Vehicle | ENTER kW Values as required |  | Qty dilution Standard for tracless vehicles |  | Number of Units | TOTAL Quantity of air required | Heatload TOTAL @ 1,2 X | Heatload Factor @ 1,2 X | Heatload Factor @ 1,5 X | Heatload Factor @ 2 X |  |  | Heat from Diesel fuel |  |  |  | Air Volume ENTER m³/s Values as required | Diesel Dilution Factor m³/s/rated kW diesel power | Total Machine kW
|  |  | 0.06 | m³/s/rated kW diesel power |  |  | 1.2 | 1.2 | 1.5 | 2 | [5 empty] | Remarks |  | 0.06
LHD - LH 621 | 345 | kW | 20.7 | m³/s | 1 | 20.7 | 414 | 414 | 517.5 | 690 | kW |  | Engine fuel consuption | 32.52 | kg/hour |  | 10 | 0.06 | 166.6667
LHD - LH 517 | 330 | kW | 19.8 | m³/s | 1 | 19.8 | 396 | 396 | 495 | 660 | kW |  | Engine/s Design power rating | 123 | kW |  | 15 | 0.06 | 250
LHD - LH 514 | 256 | kW | 15.36 | m³/s | 1 | 15.36 | 307.2 | 307.2 | 384 | 512 | kW |  | The energy content of diesel fuel | 45.6 | MJ/kg |  | 20 | 0.06 | 333.3333
Dumptruck TH530 | 293 | kW | 17.58 | m³/s | 1 | 17.58 | 351.6 | 351.6 | 439.5 | 586 | kW |  | Energy released by machine/s | 1482.912 | MJ/hr | Engine/s burns 1482,912 MJ per hour at full rated power | 25 | 0.06 | 416.6667
Dumptruck TH540 | 375 | kW | 22.5 | m³/s | 1 | 22.5 | 450 | 450 | 562.5 | 750 | kW |  | Energy released by fuel | 411.92 | kW |  | 30 | 0.06 | 500
Spraymec 1050 WPC HD | 155 | kW | 9.3 | m³/s | 1 | 9.3 | 186 | 186 | 232.5 | 310 | kW |  | Engine/s efficiency | 29.8602 | % |  | 35 | 0.06 | 583.3333
Sandvik DD420-60 Drill Rig | 110 | kW | 6.6 | m³/s | 1 | 6.6 | 132 | 132 | 165 | 220 | kW |  | Average machine/s duty cycle | 60% |  |  | 40 | 0.06 | 666.6667
Toyota Hilux LDV 2.5D4D | 75 | kW | 4.5 | m³/s | 1 | 4.5 | 90 | 90 | 112.5 | 150 | kW |  | The amount of heat produced by machine/s on average | 247.152 | kW |  | 45 | 0.06 | 750
Toyota Hilux LDV 2.7D4D | 118 | kW | 7.08 | m³/s | 1 | 7.08 | 141.6 | 141.6 | 177 | 236 | kW |  |  |  |  | Engine/s burns | 50 | 0.06 | 833.3333
Toyota Hilux LDV 3.0D4D | 120 | kW | 7.2 | m³/s | 1 | 7.2 | 144 | 144 | 180 | 240 | kW |  |  |  |  | MJ per hour at full rated power | 55 | 0.06 | 916.6667
[5 empty] | 1 | 0 | 0 | 0 |  | 0 | kW |  | Note: the specific gravity of diesel fuel oil lies in the range of 0.82 to 0.95. Ave 0.88 |  |  |  | 60 | 0.06 | 1000
|  | kW | 0 | m³/s | 1 | 0 | 0 | 0 | 0 | 0 | kW | [5 empty] | 65 | 0.06 | 1083.3333
CAT- 2900 | 320 | kW | 19.2 | m³/s | 5 | 96 | 1920 | 384 | 480 | 640 | kW | [5 empty] | 70 | 0.06 | 1166.6667
CAT- MT6020 | 567 | kW | 34.02 | m³/s | 3 | 102.06 | 2041.2 | 680.4 | 850.5 | 1134 | kW | [5 empty] | 75 | 0.06 | 1250
Nor-1610B | 120 | kW | 7.2 | m³/s | 6 | 43.2 | 864 | 144 | 180 | 240 | kW | [5 empty] | 80 | 0.06 | 1333.3333
Nor-1610B | 120 | kW | 7.2 | m³/s | 2 | 14.4 | 288 | 144 | 180 | 240 | kW | [5 empty] | 85 | 0.06 | 1416.6667
Nor-6050WP | 96 | kW | 5.76 | m³/s | 2 | 11.52 | 230.4 | 115.2 | 144 | 192 | kW | [5 empty] | 90 | 0.06 | 1500
Nor-LF600 | 155 | kW | 9.3 | m³/s | 5 | 46.5 | 930 | 186 | 232.5 | 310 | kW | [5 empty] | 95 | 0.06 | 1583.3333
CAT-12F | 108 | kW | 6.48 | m³/s | 3 | 19.44 | 388.8 | 129.6 | 162 | 216 | kW | [5 empty] | 100 | 0.06 | 1666.6667
CAT –IT38 | 134 | kW | 8.04 | m³/s | 3 | 24.12 | 482.4 | 160.8 | 201 | 268 | kW | Twin 55 |  |  |  |  | 105 | 0.06 | 1750
LDV | 120 | kW | 7.2 | m³/s | 15 | 108 | 2160 | 144 | 180 | 240 | kW | 75 |  |  |  |  | 110 | 0.06 | 1833.3333
|  | kW | 0 | m³/s | 1 | 0 | 0 | 0 | 0 | 0 | kW | 75 |  |  |  |  | 115 | 0.06 | 1916.6667
|  | kW | 0 | m³/s | 1 | 0 | 0 | 0 | 0 | 0 | kW | Twin 55 |  |  |  |  | 120 | 0.06 | 2000
[12 empty] | Twin 55 |  |  |  |  | 125 | 0.06 | 2083.3333
[12 empty] | 90 |  |  |  |  | 130 | 0.06 | 2166.6667
[12 empty] | 90+90 |  |  |  |  | 135 | 0.06 | 2250
[6 empty] | Fan KW | Fan Qty m³/s |  |  |  |  | 90+90 |  |  |  |  | 140 | 0.06 | 2333.3333
[12 empty] | 0 |  |  |  |  | 145 | 0.06 | 2416.6667
Vehicle kW Minimum Qty Calculator | [5 empty] | 45 | 12.5 | m³/s |  |  |  | 0 |  |  |  |  | 150 | 0.06 | 2500
Reject Temperature | [5 empty] | 45 (1220mm) | 20 | m³/s |  |  |  | 0 |  |  |  |  | 155 | 0.06 | 2583.3333
Wet Bulb | 27 | °C |  |  |  | 55 | 25 | m³/s |  |  |  | 0 |  |  |  |  | 160 | 0.06 | 2666.6667
Dry Bulb | 36 | °C |  |  |  | Twin 55 | 35 | m³/s |  |  |  | 0 |  |  |  |  | 165 | 0.06 | 2750
BP | 122 | Kpa |  |  |  | 75 | 32 | m³/s | [8 empty] | 170 | 0.06 | 2833.3333
Vapour Press (Pw) | 2.8565 | Kpa |  |  |  | Twin 55 | 38 | m³/s | [8 empty] | 175 | 0.06 | 2916.6667
Moisture Content ( r ) | 0.014913 | g/Kg |  |  |  | 90 | 42 | m³/s | [8 empty] | 180 | 0.06 | 3000
Moisture Content ( g/Kg ) | 14.9125 | g/Kg |  |  |  | 90+90 | 50 | m³/s | [8 empty] | 185 | 0.06 | 3083.3333
Specific Volume ( v ) | 0.7447 | m³/Kg | [14 empty] | 190 | 0.06 | 3166.6667
Density ( w ) | 1.3628 | Kg/m³ | [14 empty] | 195 | 0.06 | 3250
Enthalpy ( H ) | 74.4425 | Kj/Kg | [14 empty] | 200 | 0.06 | 3333.3333
Sigma Heat ( S ) | 72.7595 | Kj/Kg | [14 empty] | 205 | 0.06 | 3416.6667
Relative Humidity | 48.1044 | % | [14 empty] | 210 | 0.06 | 3500
Dewpoint Temperature ( tdp ) | 14.6836 | °C | [14 empty] | 215 | 0.06 | 3583.3333
Intake Temperature | [16 empty] | 220 | 0.06 | 3666.6667
Wet Bulb | 23 | °C | [14 empty] | 225 | 0.06 | 3750
Dry Bulb | 30 | °C | [14 empty] | 230 | 0.06 | 3833.3333
BP | 122 | Kpa | [14 empty] | 235 | 0.06 | 3916.6667
Vapour Press (Pw) | 2.2581 | Kpa | [14 empty] | 240 | 0.06 | 4000
Moisture Content ( r ) | 0.01173 | g/Kg | [14 empty] | 245 | 0.06 | 4083.3333
Moisture Content ( g/Kg ) | 11.7296 | g/Kg | [14 empty] | 250 | 0.06 | 4166.6667
Specific Volume ( v ) | 0.7266 | m³/Kg | [14 empty] | 255 | 0.06 | 4250
Density ( w ) | 1.3924 | Kg/m³ | [14 empty] | 260 | 0.06 | 4333.3333
Enthalpy ( H ) | 60.1192 | Kj/Kg | [14 empty] | 265 | 0.06 | 4416.6667
Sigma Heat ( S ) | 58.9915 | Kj/Kg | [14 empty] | 270 | 0.06 | 4500
Relative Humidity | 53.2443 | % | [14 empty] | 275 | 0.06 | 4583.3333
Dewpoint Temperature ( tdp ) | 12.3305 | °C | [14 empty] | 280 | 0.06 | 4666.6667
End Heatload /m | 0.05 | kW/m | [14 empty] | 285 | 0.06 | 4750
End Length | 300 | m | [14 empty] | 290 | 0.06 | 4833.3333
End Heatload | 15 | kW | [14 empty] | 295 | 0.06 | 4916.6667
Q = Vehicle kW | 256 | kW | [14 empty] | 300 | 0.06 | 5000
Heatload Factor | 1.5
Closest fan (kW) to meet Intake Qty | 55 | kW
End Heatload | 384 | kW
Total Heatload | 454 | kW
Qty Dilution Requirement | 0.06 | m³/s
Qty Required (kW x Dilution Requirement) | 15.36 | m³/s
Leakage % | 10% | /100m
Expected Leakage over distance "Total Leakage" | 30 | %
Massflow in end | 21.3876 | kg/s
kg/s Airflow Required | 32.975 | kg/s
Discharge Qty Required | 23.6817 | m³/s
Fan Intake Qty Required | 30.7863 | m³/s
Summary of Diesel Ventilation Air Requirements throughout the World
The legal requirements for ventilation air for diesel equipment vary throughout the world.
The requirements for various countries are summarised in the following table.
Country | Type of Mine | Diesel factor m³/s per kW | Other comments
Australia
New South Wales | Coal | 0.063 | Minimum airflow 4.7 m3/s
Queensland | Coal | 0.04 | Minimum airflow 2.5 m3/s
South Australia | All mines | 0.032 | Minimum airflow 2.4 - 4.7 m3/s
Victoria | All mines | 0.031 | Minimum airflow 2.4.7 m3/s
Western Australia | All mines | 0.063
Canada
Maniitoba | Not specified | 0.047
Newfoundland | Not specified | 0.05
Ontario | Not specified | 0.06
Quebec | Not specified | 0.092
Saskatchewan | All mines | 0.063
Yukon Territory | Not specified | 0.047 | 0.05 m3/s per person and max velocity 2.5 m/s
Chile | Not specified | 0.134 | For 0.08% < CO < 0.12%
Columbia |  | 0.089 | For CO<0.08%
Germany
Lower Saxony | Coal | 0.057
North Rhine- Westphalia |  | 0.068 | CO <0.06%
| Non gassy | 0.092 | For 0.06% < CO < 0.08%
| Hard coal | 0.137 | For 0.08% < CO < 0.12%
Ireland | Non hard coal | 0.063
India | Hard coal |  | Min airflow 2.83 m3/s
Korea | Coal |  | 0.05 m3/s per person
Mexico | Coal | 0.268 | 0.05 m3/s per person
New Zealand | Coal |  | Min airflow 4.7 m3/s
Philippines | Not specified | 0.047 | Min airflow 0.33 m3/s
Romania | Coal |  | CO < 0.06%, min airflow 0.05m3/s
| Coal |  | For 0.06% < CO < 0.08%, min airflow 0.067 m3/s
| Coal |  | For 0.08% < CO < 0.12%, min airflow 0.100 m3/s
Spain | Not specified | 0.24
Sweden | Not specified | 0.034 | Depends on fuel and airway size
0.169
United States | All mines | 0.02 | Equipment tested for minimum air quality to reduce the highest gaseous emission [CO, NO, No2, or CO2]to its safe level for 8 hour exposure [ACGIH}. Defined as ‘nameplate’ quantity to be delivered to operating equipment. Nameplate quantities for approved equipment range from 0.02m³/kW to 0,07m³/s
0.07
Zambia | All mines | 0.05
MHSA also specifies minimum air quantity to achieve Diesel Particulate Matter [DPM] level of 1.0 mg/m3[range is from 0.01 m3/s/kW to 0.18 m3/s/kW. Current proposal relates to DPM level of 0.16 mg/m3.
Canada has similar certification rules but generally higher than MHSA [e.g. Deutz BF6M 1013: MHSA – 0.29 m3/kW Canmet – 0.059 m3/kW].
Other countries [e.g. Germany, Austria] specify DPM levels; These have to complied with by ventilation and filtration.
Mine Health and Safety Act regulations current specify the gaseous occupational exposure levels [OELs] of diesel exhaust to which employees may be exposed, see Table 1 below.
Table 1 | MHSA OELs for diesel gases
Substance | OEL | OEL-STEL/OEL-C
CO limit | 30 ppm | 100 ppm [OEL-C]
CO2 | 5000 ppm | 30 000 ppm [OEL-C]
NOx | 25 ppm | 35 ppm [OEL-STEL]
So2 | 2 ppm | 5 ppm [OEL-STEL
Currently there are no specific regulations for controlling DPM. The Occupational Hygiene Sub Committee [Technical Task Team on Diesel Particulate Matter] recommended that a value of 1.5 mg/m3 be used as a preliminary target and that Respirable Combustible Dust [RCD] method be used by mines to establish their baselines. This method measures the exposure of workers to DPM.
Note on C7: Johan van Sittert: Note Engine kW may Vary
Note on C8: Johan van Sittert: Note Engine kW may Vary 280-330kW
Note on C9: Johan van Sittert: Note Engine kW may Vary
Note on C10: Johan van Sittert: Note Engine kW may Vary
Note on C11: Johan van Sittert: Note Engine kW may Vary
Note on C12: Johan van Sittert: Note Engine kW may Vary
Note on C13: Johan van Sittert: Note Engine kW may Vary
Note on C14: Johan van Sittert: Note Engine kW may Vary
Note on C15: Johan van Sittert: Note Engine kW may Vary
Note on C16: Johan van Sittert: Note Engine kW may Vary
Note on C17: Johan van Sittert: Note Engine kW may Vary
Note on C18: Johan van Sittert: Note Engine kW may Vary
Note on C19: Johan van Sittert: Note Engine kW may Vary
Note on C20: Johan van Sittert: Note Engine kW may Vary
Note on C21: Johan van Sittert: Note Engine kW may Vary
Note on C22: Johan van Sittert: Note Engine kW may Vary
Note on C23: Johan van Sittert: Note Engine kW may Vary
Note on C24: Johan van Sittert: Note Engine kW may Vary
Note on C25: Johan van Sittert: Note Engine kW may Vary
Note on C26: Johan van Sittert: Note Engine kW may Vary
Note on C27: Johan van Sittert: Note Engine kW may Vary
Note on C28: Johan van Sittert: Note Engine kW may Vary
Note on C29: Johan van Sittert: Note Engine kW may Vary
Note on C67: Johan van Sittert:

## Airflow Measurement
Back to INDEX
AIRFLOW MEASUREMENT
Pitot tube positions in a circular duct | [9 empty] | VELOCITY from VELOCITY PRESSURE (Pitot Tube Readings)
Rn | = |  |  |  | Pitot Tube marks |  |  |  |  | V | =
Where | [5 empty] | Point | Diameter Radius |  | Pitot Tube Mark | Measurements around perimeter |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
n | 7 | .'th | = | the nth reading from the centre |  | 1 | 790.5694 | mm | 1709.4306 |  | air density [kg/m3] | Point | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s | Pitot Tube VP | Vel m/s
d | 5000 | mm | = | duct diameter [mm] |  | 2 | 1369.3064 | mm | 1130.6936 |  | 1.0998 | 1 | 130 | 15.3757 | 130 | 15.3757
N | 10 |  | = | number of readings across a diameter |  | 3 | 1767.767 | mm | 732.233 | d = duct diameter [mm] | 5500 | 2 | 130 | 15.3757 | 170 | 17.5828
Rn | 2850.4386 | radius of the reading [mm] |  |  |  | 4 | 2091.6501 | mm | 408.3499 |  | Duct Diameter (m) | 3 | 120 | 14.7725
[6 empty] | 5 | 2371.7082 | mm | 128.2918 |  | 5.5 | 4 | 110 | 14.1436
[6 empty] | 6 | 2622.0221 | mm | -122.0221 | Measurements at fan |  | 5
VELOCITY PRESSURE (Bernoulli's Equation) | [5 empty] | 7 | 2850.4386 | mm | -350.4386 | Barometric Pressure kPa | 99 | 6
[6 empty] | 8 | 3061.8622 | mm | -561.8622 | Fan Total Pressure kPa | 3.89 | 7
VP | = |  |  |  |  | 9 | 3259.6012 | mm | -759.6012 | Δ Pressure kPa | 95.11 | 8
Where | [5 empty] | 10 | 3446.0122 | mm | -946.0122 | Temp Wetbulb | 24.5 | 9
V | 5 | = | air velocity [m/s] | [6 empty] | Temp Drybulb | 24.5 | 10
w | 1.152 | = | air density [kg/m3] |  |  | If full length needs to be traversed with one pitot tube |  |  |  |  | Duct Mean Velocity m/s |  | 15.4377
VP | 14.4 | velocity pressure [Pa] |  |  |  | Point | Half Way | Diameter Radius |  |  | Duct Area m² |  | 23.7583
[6 empty] | 6 | 2500 | 2628.2918 | mm |  | Volume m³/s |  | 366.7734
[6 empty] | 7 |  | 2908.3499 | mm |  | Massflow kg/s |  | 403.366
VELOCITY from VELOCITY PRESSURE (Bernoulli's Equation) | [5 empty] | 8 |  | 3232.233 | mm
[6 empty] | 9 |  | 3630.6936 | mm
V | = |  |  |  |  | 10 |  | 4209.4306 | mm
Where
VP | 200 | = | velocity pressure [Pa] | [6 empty] | 4 Point method
w | 1.152 | = | air density [kg/m3] | [6 empty] | Duct mm Diameter | Reading (mm) | Number from side
Vel | 18.6339 | air velocity [m/s] | [7 empty] | 5500
[10 empty] | 0.024 | 132 | 1
[10 empty] | 0.1 | 550 | 2
Bernoulli’s Theorem [for frictionless flow] | [9 empty] | 0.194 | 1067 | 3
TP1 | = | TP2 | [7 empty] | 0.334 | 1837 | 4
or
VP1 + SP1 | = | VP2 + SP2
Because
| TP | = | SP + VP
Where | TP | = | Total pressure
| SP | = | Static Pressure
| VP | = | Velocity Pressure
Where
SP | 800 | Static Pressure
VP | 150 | Velocity Pressure
TP | 950 | Total pressure
3 Point method
BAROMETRIC PRESSURE INCREASE OR DECEASE | [9 empty] | Duct mm Diameter | Reading (mm) | Number from side
The approximate barometric pressure increase or decease in a vertical shaft = 1 kPa/100m | [9 empty] | 7100
[10 empty] | 0.032 | 227.2 | 1
[10 empty] | 0.137 | 972.7 | 2
VELOCITY PRESSURE | [9 empty] | 0.312 | 2215.2 | 3
| VP | =
Where | VP | = | velocity pressure [Pa]
| V | = | air velocity [m/s]
| w | = | air density [kg/m3]
ø2000mm
1
2
3
4
Note on C8: REMEMBER - READINGS ACROSS DIAMETER!! Note! Use Even Numbers

## Refr+BAC+PCT Reports
Back to INDEX
XXXX Mine | [7 empty] | Mine Logo |  |  |  | XXXX Mine | [11 empty] | XXXX Mine |  |  |  |  | XXXX Mine
MONTHLY FRIDGE PLANT PERFORMANCE REPORT | [10 empty] | MONTHLY Bulk Air Cooler (BAC) PERFORMANCE REPORT | [15 empty] | Mine Logo
Mine Logo
Date: | / / 202 | [9 empty] | Date: | / / 202 | [28 empty] | Mine Logo
[24 empty] | MONTHLY Pre-Cooling Tower PERFORMANCE REPORT |  |  |  |  | VENTILATION DEPARTMENT
|  | Refrigeration machine #1 |  |  | Refrigeration machine #2 |  |  | Refrigeration machine #3 |  |  | UTILIZATION AND PERFORMANCE |  |  | Xxxxxxxxx SHAFT | [9 empty] | Date: | / / 202 |  |  |  | Refrigeration Plant Health Survey
Status |  | Unit Not Operating |  |  | Unit Operating |  |  | Unit operating | [5 empty] | BAC No.1 |  |  | BAC No.2 |  |  | BAC No.3
| Units | Design | PLC / SCADA | Measured | Design | PLC / SCADA | Measured | Design | PLC / SCADA | Measured | BULK AIR COOLER PERFORMANCE |  | Units | DESIGN | PLC / SCADA | Measured | DESIGN | PLC / SCADA | Measured | DESIGN | PLC / SCADA | Measured |  | PRE-COOLING TOWER | Units | DESIGN | PLC / SCADA | Measured | Production Manager | [8 empty] | Date |  |  | / / 202
Evaporator duty | kW | 7536.6 | 0 | 0 | 7536.6 | 0 | 0 | 7536.6 | 0 | 0 | BAROMETRIC PRESSURE |  | KPa | 89 | [9 empty] | WATER TEMP IN | °C | 28 | 24.77 | 24.77 | Section Engineer | [8 empty] | Report Ref. No.
Evaporator flow | l/s | 360 |  |  | 360 |  |  | 360 |  |  | WATER TEMP IN |  | °C | 5 | [9 empty] | WATER TEMP OUT | °C | 23 | 20.89 | 20.89 | Section Engineering Manager
Chilled water in | °C | 20 |  |  | 20 |  |  | 20 |  |  | WATER TEMP OUT |  | °C | 13.4 | [9 empty] | WATER FLOW | l/s | 200 | 112 | 112 | Engineering Foreman
Chilled water out | °C | 15 |  |  | 15 |  |  | 15 |  |  | WATER FLOW |  | l/s | 425 | [8 empty] | Eff WATER | DUTY (WATER CIRCUIT) | kW | 4187 | 1819.5027 | 1819.5027 | Shaft Ventilation Engineer
Suction pressure | kPa | 350 |  |  | 350 |  |  | 350 |  |  | DUTY (WATER CIRCUIT) |  | kW | 14947.59 | 0 | 0 | 2750 | 0 | 0 | 2750 | 0 | 0 | 0% | WETBULB TEMP IN | °C | 18.5 | 20.21 | 20.21 | Ventilation Officer
Saturated evaporator temp | °C | [9 empty] | WETBULB TEMP IN |  | °C | 30 | [9 empty] | DRYBULB TEMP IN | °C | 32 | 35 | 35
Evaporating temperature | °C | 13 |  |  | 13 |  |  | 13 |  |  | DRYBULB TEMP IN |  | °C | 30 | [9 empty] | BAROMETRIC PRESSURE | KPa | 90.5 | 90 | 90 | SKETCH (Not to scale) | [11 empty] | Indicate Wind Direction on Wind Rose below
Small temperature difference | °C | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | Density ( w ) |  |  | 1.0045 | -0.0029437 | -0.0029437 |  | -0.0029437 | -0.0029437 |  | -0.0029437 | -0.0029437 |  | Density ( w ) |  | 1.0276 | 1.0112 | 1.0112
[11 empty] | Vapour Press (Pw) |  |  | 4.241 | 0.6105 | 0.6105 |  | 0.6105 | 0.6105 |  | 0.6105 | 0.6105 |  | Vapour Press (Pw) |  | 1.3419 | 1.5105 | 1.5105
Condenser duty | kW | 9420.75 | 0 | 0 | 9420.75 | 0 | 0 | 9420.75 | 0 | 0 | Moisture Content ( r ) |  |  | 0.031122 | -0.622 | -0.622 |  | -0.622 | -0.622 |  | -0.622 | -0.622 |  | Moisture Content ( r ) |  | 0.0093618 | 0.010617 | 0.010617
Condenser flow | l/s | 450 |  |  | 450 |  |  | 450 |  |  | Moisture Content ( g/Kg ) |  |  | 31.1222 | -622 | -622 |  | -622 | -622 |  | -622 | -622 |  | Moisture Content ( g/Kg ) |  | 9.3618 | 10.6171 | 10.6171
Cooling water in | °C | 24 |  |  | 24 |  |  | 24 |  |  | Specific Volume ( v ) |  |  | 1.0265 | -128.4096 | -128.4096 |  | -128.4096 | -128.4096 |  | -128.4096 | -128.4096 |  | Specific Volume ( v ) |  | 0.98228 | 0.99943 | 0.99943
Cooling water out | °C | 29 |  |  | 29 |  |  | 29 |  |  | Enthalpy ( H ) |  |  | 109.6673 | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | Enthalpy ( H ) |  | 56.113 | 62.3973 | 62.3973
Condenser pressure | kPa | 1250 |  |  | 1250 |  |  | 1250 |  |  | Sigma Heat ( S ) |  |  | 105.7646 | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | Sigma Heat ( S ) |  | 55.3891 | 61.5004 | 61.5004
Saturated condenser temp | °C | 37 |  |  | 37 |  |  | 37 |  |  | Relative Humidity |  |  | 100 | 100 | 100 |  | 100 | 100 |  | 100 | 100 |  | Relative Humidity |  | 28.2365 | 26.8769 | 26.8769
Condensing temperature | °C | 35 |  |  | 35 |  |  | 35 |  |  | Dewpoint Temp °C (tdp ) |  |  | 18.7414 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | Dewpoint Temp °C (tdp ) |  | 7.2742 | 8.4056 | 8.4056
Discharge temperature | °C | 40 |  |  | 40 |  |  | 40 |  |  | WETBULB TEMP OUT |  | °C | 10.6 | [9 empty] | WETBULB TEMP OUT | °C | 23 | 22.3 | 22.3
Oil temperature | °C | 60 |  |  | 60 |  |  | 60 |  |  | DRYBULB TEMP OUT |  | °C | 10.6 | [9 empty] | DRYBULB TEMP OUT | °C | 25.5 | 24 | 24
Small temperature difference | °C | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | BAROMETRIC PRESSURE |  |  | 89 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | BAROMETRIC PRESSURE | KPa | 90.5 | 90 | 90
[11 empty] | Density ( w ) |  |  | 1.0869 | -0.0029437 | -0.0029437 |  | -0.0029437 | -0.0029437 |  | -0.0029437 | -0.0029437 |  | Density ( w ) |  | 1.0441 | 1.0438 | 1.0438
Compressor and motor |  |  | PLC |  |  | PLC |  |  | PLC |  | Vapour Press (Pw) |  |  | 1.2776 | 0.6105 | 0.6105 |  | 0.6105 | 0.6105 |  | 0.6105 | 0.6105 |  | Vapour Press (Pw) |  | 2.6624 | 2.5928 | 2.5928
PRV position |  | 0 - 100% |  |  | 0 - 100% |  |  | 0 - 100% |  |  | Moisture Content ( r ) |  |  | 0.0090588 | -0.622 | -0.622 |  | -0.622 | -0.622 |  | -0.622 | -0.622 |  | Moisture Content ( r ) |  | 0.018853 | 0.018451 | 0.018451
Absorbed power (using electrical) | kWe | 1225.1748 | 0 |  | 1991.945 | 0 |  | 1991.945 | 0 |  | Moisture Content ( g/Kg ) |  |  | 9.0588 | -622 | -622 |  | -622 | -622 |  | -622 | -622 |  | Moisture Content ( g/Kg ) |  | 18.8528 | 18.4507 | 18.4507
Absorbed power (using process) | kWe | 1983.3158 | #DIV/0! |  | 1983.3158 | #DIV/0! |  | 1983.3158 | #DIV/0! |  | Specific Volume ( v ) |  |  | 0.92834 | -128.4096 | -128.4096 |  | -128.4096 | -128.4096 |  | -128.4096 | -128.4096 |  | Specific Volume ( v ) |  | 0.97581 | 0.97569 | 0.97569
Motor duty | kWs | 1884.15 | 0 |  | 1884.15 | 0 |  | 1884.15 | 0 |  | Enthalpy ( H ) |  |  | 33.4819 | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | Enthalpy ( H ) |  | 73.6436 | 71.0624 | 71.0624
Motor current | A | 71.45 |  |  | 205 |  |  | 205 |  |  | Sigma Heat ( S ) |  |  | 33.0805 | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | -1555.622 | -1555.622 |  | Sigma Heat ( S ) |  | 71.8311 | 69.3425 | 69.3425
Voltage | V | 11000 |  |  | 6600 |  |  | 6600 |  |  | Relative Humidity |  |  | 100 | 100 | 100 |  | 100 | 100 |  | 100 | 100 |  | Relative Humidity |  | 81.6234 | 86.9355 | 86.9355
PF |  | 0.9 |  |  | 0.85 |  |  | 0.85 |  |  | Dewpoint Temp °C (tdp ) |  |  | 6.8074 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | Dewpoint Temp °C (tdp ) |  | 13.9745 | 13.7088 | 13.7088
Motor efficiency |  | 0.95 |  |  | 0.95 |  |  | 0.95 | [15 empty] | Quantity of Air | m³/s | 180 | 150 | 150
COP (Plant Duty) |  | 4 | Enter Data | Enter Data |  | Enter Data | Enter Data |  | Enter Data | Enter Data | [13 empty] | Massflow (kg/s) [Measured or design] | Kg/s | 181.8 | 151.6791 | 151.6791
COP (electrical) |  | 6.1514 | #DIV/0! |  | 3.7835 | #DIV/0! |  | 3.7835 | #DIV/0! |  | AIRFLOW |  | m3/s | 250 |  | 244 |  |  | 234 |  |  | 238 |  | DUTY (AIR CIRCUIT) | kW | 1500 | 1189.4809 | 1189.4809
COP (process) |  | 3.8 | #DIV/0! |  | 3.8 | #DIV/0! |  | 3.8 | #DIV/0! |  | MASSFLOW |  | kg/s | 500 | 0 | -0.71826 |  | 0 | -0.68883 |  | 0 | -0.7006 | Eff AIR | EFFICIENCY | % | 90% | 85.09% | 85.09% | Legend
General (list alarms, trips, general issues observed) | [10 empty] | DUTY (AIR CIRCUIT) |  | kW | 14360 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [6 empty] | Door
[11 empty] | EFFICIENCY |  | %
[24 empty] | General (list alarms, trips, general issues observed) | [5 empty] | Eye and Shower wash stations
General (list alarms, trips, general issues observed)
Fire Extinguisher
Fire Hose Reel
|  | TOWER NO.1 |  |  | TOWER NO.2 |  |  | TOWER NO.3 | [21 empty] | Wind Sock
CONDENSER COOLING TOWERS | Units | DESIGN | SCADA | Actual | DESIGN | SCADA | Actual | DESIGN | SCADA | Actual
WATER FLOW | l/s | 400 |  |  | 400 |  |  | 400 | [21 empty] | EMERGENCY Stop
WATER TEMP IN | °C | 29 |  |  | 29 |  |  | 29
WATER TEMP OUT | °C | 24 |  |  | 24 |  |  | 24 | [21 empty] | Tower Louvres
DUTY | kW | 8374 |  |  | 8374 |  |  | 8374
PERFORMANCE INDEX
[29 empty] | Environmental Conditions | [5 empty] | Eye Wash and Shower stations
Notes: | [28 empty] | Ref Number | Area Description | Noise |  | Illumination |  | Ref Number | Area Description |  | Wash Basin Operational |  |  | Eyewash basin Operational | Wash basin demarcated | Wash basin water pressure adequate
[31 empty] | dB(A) | Source | Lux | Type
[29 empty] | 1 | [5 empty] | A
[29 empty] | 2 | [5 empty] | B
[29 empty] | 3 | [5 empty] | C
[29 empty] | 4 | [5 empty] | D
[29 empty] | 5 | [5 empty] | E
[29 empty] | 6 | [5 empty] | F
[29 empty] | 7 | [5 empty] | G
[29 empty] | 8 | [5 empty] | H
[29 empty] | 9 | [5 empty] | I
[29 empty] | 10 | [5 empty] | J
Fire Protection and Prevention
[29 empty] | Fire Extinguishers | [7 empty] | Electrical construction
[29 empty] | Ref Number | Condition | Expiry Date | Monthly inspection conducted | Symbolic Signs | Type of Extinguisher | Size of Extinguisher |  | Ref Number | MSDS Available |  | Bundwall Capacity demarcated | Bundwall aggregate installed | Bundwall capacity (≥ 110% of Liquid) | Drain pipe and Valve installed (Closed)
[29 empty] | K |  |  | YES | YES |  |  |  | 11
[29 empty] | L |  |  | YES | YES |  |  |  | 12
[29 empty] | N |  |  | YES | YES |  |  |  | 13
[29 empty] | O |  |  | YES | YES |  |  |  | 14
[29 empty] | P |  |  | YES | YES |  |  |  | 15
[29 empty] | Q |  |  | YES | YES |  |  |  | FireHose Reel
[29 empty] | R |  |  | YES | YES |  |  |  | Ref Number | Condition |  | Monthly inspection conducted | Operational | Symbolic Signs Installed | Hose Nozzle installed
[29 empty] | S |  |  | YES | YES
[29 empty] | T |  |  | YES | YES |  |  |  | 16
[29 empty] | U |  |  | YES | YES |  |  |  | 17
[29 empty] | V |  |  | YES | YES |  |  |  | 18
[29 empty] | X |  |  | YES | YES |  |  |  | 19
[29 empty] | Y |  |  | YES | YES |  |  |  | 20
[29 empty] | Z |  |  | YES | YES |  |  |  | 21
[29 empty] | Fire fighting method |  |  |  | Fire Hose Reel | AUTOMATED SPRINKLER SYSTEM | FIRE HYDRANT | MANUAL SPRINKLER SYSTEM |  | Water supply operational |  |  |  | YES
Water pressure (Pa)
General
[29 empty] | Escape & Emergency |  |  |  | Fire Hazards |  |  |  |  | Hearing Protection Type |  |  | CHPD's | Reusable HPD's | Disposable HPD's
[29 empty] | Emergency Procedures |  | DISPLAYED |  | Electrical |  |  | OBSERVED Yes / No |  | Number of Hearing Protection worn |  |  | X out XX | X out XX | X out XX
[29 empty] | Escape Strategy |  | DISPLAYED | [6 empty] | Noise Zone Demarcation
[29 empty] | Escape route demarcated |  | YES |  | Waste |  |  | OBSERVED Yes / No |  | Breathing Apparatus Available
[29 empty] | Escape drills conducted |  | YES | [6 empty] | Adequate number available
[29 empty] | Escape route unobstructed |  |  |  | Combustible Material |  |  | OBSERVED Yes / No |  | Last inspection on Breathing Apparatus
[29 empty] | Emergency Assembly Area Demarcated | [8 empty] | Floor surface
[29 empty] | Audible Evacuation Siren Available |  |  |  | Other |  |  | OBSERVED Yes / No |  | Drinking Water within reasonble distance
[29 empty] | Last tested | [8 empty] | Housekeeping
[29 empty] | Ammonia Sensors |  | YES |  | Remarks regarding Fire Hazards: |  |  |  |  | First Aid tube available
[29 empty] | NH3 Calibration certificates available |  | YES | [6 empty] | Last inspection
Windsock Available
[29 empty] | Number | INSTRUCTION / ACTION REQUIRED | [8 empty] | RESPONSIBLE PERSON |  | SIGNATURE | COMPLETION DATE
[30 empty] | Ventilation Officer | [7 empty] | Engineering Foreman
[30 empty] | Date: | [7 empty] | Date:
Section Engineer
[30 empty] | Sectional Ventilation Officer | [7 empty] | Date:
Date:
Section Engineering Manager
Date:
Production Manager
[30 empty] | Shaft Ventilation Engineer | [7 empty] | Date:
Date:
A
D
N
Note on E9: Data Obtained from Electronic monitoring System
Note on F9: Data Obtained by physical measuring with calibrated instruments
Note on H9: Data Obtained from Electronic monitoring System
Note on I9: Data Obtained by physical measuring with calibrated instruments
Note on K9: Data Obtained from Electronic monitoring System
Note on L9: Data Obtained by physical measuring with calibrated instruments
Note on T9: Data Obtained from Electronic monitoring System
Note on U9: Data Obtained by physical measuring with calibrated instruments
Note on W9: Data Obtained from Electronic monitoring System
Note on X9: Data Obtained by physical measuring with calibrated instruments
Note on Z9: Data Obtained from Electronic monitoring System
Note on AA9: Data Obtained by physical measuring with calibrated instruments
Note on AH9: Data Obtained from Electronic monitoring System
Note on AI9: Data Obtained by physical measuring with calibrated instruments
Note on AS57: AMMONIA Plants

## Planning Tool (Old)
HEAT AND COOLING CALCULATIONS
INPUTS | Year 1 | Section X | [5 empty] | Section Y | [5 empty] | Section Z
VENTILATION DISTRICT | TOT/AVE | PLAN |  | AIR |  | KT |  | PLAN |  | AIR |  | KT |  | PLAN |  | AIR |  | KT
MONTHLY PROD. RATE IN KT/MONTH STOPING | 40 | 15 |  | 15 |  | 20.2777 | 20.2777 | 0 |  | 0 |  | 1.4709 | 1.4709 | 25 |  | 25 |  | 28.5781 | 28.5781
MONTHLY PROD. RATE IN KT/MONTH DEV. | 46.9 | 7 |  | 7 |  | 0 |  | 18.2 |  | 18.2 |  | 0 |  | 21.7 |  | 21.7 |  | 0
TOTAL PRODUCTION DEV+STOPING KT/MONTH | 86.9 | 22 | 0 | 22 | 0 | 20.2777 | 20.2777 | 18.2 | 0 | 18.2 | 0 | 1.4709 | 1.4709 | 46.7 | 0 | 46.7 | 0 | 28.5781 | 28.5781
MEAN ROCK BREAKING DEPTH IN METERS |  | 1650 |  | 1650 |  | 1650 |  | 3052 |  | 3052 |  | 3052 |  | 3052 |  | 3052 |  | 3052
AVE. DIST. FROM THE SHAFT IN METERS |  | 1500 |  | 1500 |  | 1500 |  | 1400 |  | 1400 |  | 1400 |  | 1400 |  | 1400 |  | 1400
NO. OF LOCOMOTIVES (BASED UPON KW/Kt) |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
NO. OF MEN (BASED UPON KW/Kt) |  | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3 | 5 | 3
ACTUAL HEAT FROM ELECTRICAL ENERGY KW/Kt |  | 38.2 | 10 | 38.2 | 10 | 38.2 | 10 | 38.2 | 10 | 38.2 | 10 | 38.2 | 10 | 68 | 10 | 68 | 10 | 68 | 10
AIR VOLUME (EXCLUDING LEAKAGE) IN M3/S | 595 | 70 |  | 65.7644 |  | 70 |  | 25 |  | 24.7818 |  | 25 |  | 500 |  | 462.4538 |  | 500 |  |  | 0
REQUIRED M/FLOW AT (Input Value C14) KG/S/KT |  | 44 | 0 | 44 | 0 | 40.5555 | 40.5555 | 36.4 | 0 | 36.4 | 0 | 2.9417 | 2.9417 | 93.4 | 0 | 93.4 | 0 | 57.1563 | 57.1563
DESIGN AIR KG/S/KT |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
DESIGN WATER TONNE/TONNE |  | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
SERVICE WATER USED FOR COOLING Y=1 N=0 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SURFACE BAC WORKING YES=1 NO=0 |  | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0
Service Water Availability (l/s) |  |  | 0 |  |  |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  |  |  | 0
BULK AIR COOLER WATER AVAILABLE IN L/S-TOTAL |  |  | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0
BULK AIR COOLER DELTA WATER TEMPERATURE |  |  | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0
Amount of Cooling Cars to be installed @ 6L/sec |  | 1.68 |  | 1.68 |  |  |  | 13 |  | 13 |  |  |  | 16.2 |  | 16.2
COOL. CAR WATER AVAILABLE IN L/S-TOTAL |  | 10.08 | 10.08 | 10.08 | 10.08 |  |  | 78 | 78 | 78 | 78 |  |  | 97.2 | 97.2 | 97.2 | 97.2
COOL. CAR DELTA WATER TEMPERATURE |  | 11 | 11 | 11 | 11 |  |  | 14.2 | 14.2 | 14.2 | 14.2 |  |  | 14.2 | 14.2 | 14.2 | 14.2
DESIGN WATER DELTA TEMPERATURE OF SERVICE WATER |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
SECTION AIR UTILIZATION IN % |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Geothemal gradient (Eg.: 0.0113) |  | 0.0113 | [5 empty] | 0.0113 | 0.0113 | 0.0113 | 0.0113 |  |  | 0.01037
Geothemal gradient (Eg.: 21°) |  | 21 | [5 empty] | 21 | 21 | 21 | 21 |  |  | 21
Surface BP |  | 87 | 87 |  | 87 |  | 87 | 87 | 87 |  | 87 |  | 87 | 87 | 87 |  | 87 |  | 87
DESIGN REJECT TEMP WB IN DEG. C |  | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
OUTPUTS
ANALYSIS OF BEST COMBINATION
HEAT PROD. RATE IN WATTS/TONNE/MONTH |  | 99.231 | 112.6039 | 99.231 | 119.8563 | 99.231 | 119.8563 | 212.0462 | 40.4622 | 212.0462 | 40.8185 | 212.0462 | 40.8185 | 191.6072 | 37.7533 | 191.6072 | 40.8185 | 191.6072 | 40.8185
REJ. TEMP. CORRECTION PERCENT |  | 0.06 | -86.555 | 0.06 | -86.555 | 0.06 | -86.555 | 0.06 | -11.8284 | 0.06 | -11.8284 | 0.06 | -11.8284 | 0.06 | -11.8284 | 0.06 | -11.8284 | 0.06 | -11.8284
HEAT PROD. RATE CORRECTED FOR TEMP. |  | 105.1848 | 13.1875 | 105.1848 | 13.1875 | 105.1848 | 13.1875 | 224.769 | 11.435 | 224.769 | 11.435 | 224.769 | 11.435 | 203.1036 | 11.435 | 203.1036 | 11.435 | 203.1036 | 11.435
VRT °C = |  | 39.645 |  | 39.645 |  | 39.645 |  | 55.4876 |  | 55.4876 |  | 55.4876 |  | 52.6492 |  | 52.6492 |  | 52.6492
HEAT PRODUCTION IN KW FOR ROCK | 21904.5405 | 3484.4666 |  | 3484.4666 |  | 3211.6877 |  | 5059.0354 |  | 5059.0354 |  | 408.8561 |  | 13361.0385 |  | 13361.0385 |  | 8176.3088
MASSFLOW OF AIR | 708.7321 | 79.8966 |  | 75.0622 |  | 79.8966 |  | 29.9445 |  | 29.6832 |  | 29.9445 |  | 598.891 |  | 553.9188 |  | 598.891
HEAT REMOVAL CAPACITY OF AIR IN KW WITH BAC | 11748.0752 | 3192.0342 | 39.9521 | 2998.8893 | 39.9521 | 3192.0342 | 39.9521 | 407.4305 | 13.6062 | 403.8746 | 13.6062 | 407.4305 | 13.6062 | 8148.6105 | 13.6062 | 7536.7114 | 13.6062 | 8148.6105 | 13.6062
HEAT REMOVAL CAPACITY OF AIR IN KW NO BAC | 0 | 0 | 18.425 | 0 | 18.425 | 0 | 18.425 | 0 | -5.6427 | 0 | -5.6427 | 0 | -5.6427 | 0 | -5.6427 | 0 | -5.6427 | 0 | -5.6427 | 18.425
SERVICE WATER L/S | 2.5145 | 0.63657 | 0.48225 | 0.63657 | 0.48225 | 0.58674 | 0.48225 | 0.52662 | 0.48225 | 0.52662 | 0.48225 | 0.04256 | 0.48225 | 1.3513 | 0.48225 | 1.3513 | 0.48225 | 0.82691 | 0.48225
Total Water L/S Required |  | 10.7166 | [5 empty] | 78.5266 | [5 empty] | 98.5513
HEAT REM. CAP. OF SERV. WATER IN KW |  | 21.3227 | 16.1535 | 21.3227 | 16.1535 | 19.6535 | 16.1535 | 17.6397 | 16.1535 | 17.6397 | 16.1535 | 1.4256 | 16.1535 | 45.2622 | 16.1535 | 45.2622 | 16.1535 | 27.6983 | 16.1535
HEAT REM. CAP. OF BULK COOL. IN KW. |  | 0 | -15.75 | 0 | -15.75 | 0 | -15.75 | 0 | 47.34 | 0 | 47.34 | 0 | 47.34 | 0 | 47.34 | 0 | 47.34 | 0 | 47.34
HEAT REM. CAP. OF COOL. CARS IN KW |  | 464.2546 | 15.81 | 464.2546 | 15.81 | 0 | 15.81 | 4637.5212 | 12.1648 | 4637.5212 | 12.1648 | 0 | 12.1648 | 5779.0649 | 12.1648 | 5779.0649 | 12.1648 | 0 | 12.1648
TOTAL REFRIG. AVAILABLE IN KW | 10965.0652 | 485.5772 |  | 485.5772 |  | 19.6535 |  | 4655.1609 |  | 4655.1609 |  | 1.4256 |  | 5824.3271 |  | 5824.3271 |  | 27.6983
TOTAL WATER FLOW REQUIRED L/S | 187.7945 | 10.7166 |  | 10.7166 |  | 0.58674 |  | 78.5266 |  | 78.5266 |  | 0.04256 |  | 98.5513 |  | 98.5513 |  | 0.82691
TOTAL RESOURCES AVAILABLE IN KW | 22713.1405 | 3677.6115 |  | 3484.4666 |  | 3211.6877 |  | 5062.5914 |  | 5059.0354 |  | 408.8561 |  | 13972.9376 |  | 13361.0385 |  | 8176.3088
QUANTITY REQUIRED TO ACHIEVE DESIGN
WETBULB TEMPERATURE WITH BAC | 553 | 65.7644 | 1.1414 | 65.7644 | 1.1414 | 70 | 1.1414 | 24.7818 | 1.1978 | 24.7818 | 1.1978 | 25 | 1.1978 | 462.4538 | 1.1978 | 462.4538 | 1.1978 | 500 | 1.1978
ACT. MASSFLOW OF AIR PER KTONNE |  | 3.6317 |  | 3.4119 |  | 3.9401 |  | 1.6453 |  | 1.6309 |  | 20.3584 |  | 12.8242 |  | 11.8612 |  | 20.9563
HEAT PROD. RATE LESS TOTAL RESOURCES | -808.6 | -193.1449 |  | 0 |  | 0 |  | -3.556 |  | 0 |  | 0 |  | -611.8991 |  | 0 |  | 0
EXPECTED WB TEMPERATURE WITH SURFACE BAC |  | 27.9753 |  | 28.5252 |  | 28.5252 |  | 28.5041 |  | 28.5352 |  | 28.5352 |  | 28.2672 |  | 28.5352 |  | 28.5352
ADDITIONAL CALCULATIONS
EXPECTED WB TEMPERATURE WITHOUT BAC |  | 32.1261 |  | 32.5848 |  | 32.5848 |  | 33.2177 |  | 33.247 |  | 33.247 |  | 32.995 |  | 33.247 |  | 33.247
POT. Kt AT 4KG/S/Kt THAT CAN BE MINED IN AREA | 177.183 | 19.9741 | 0 | 18.7655 | 0 | 19.9741 | 0 | 7.4861 | 0 | 7.4208 | 0 | 7.4861 | 0 | 149.7227 | 0 | 138.4797 | 0 | 149.7227 | 0
ACTUAL PLANNED CENTARES | 9592.3261 | 3597.1223 | 0 | 3597.1223 | 0 | 4862.7689 | 4862.7689 | 0 | 0 | 0 | 0 | 352.7265 | 352.7265 | 5995.2038 | 0 | 5995.2038 | 0 | 6853.2708 | 6853.2708
POTENTIAL CENTARES IF AIR IS USED FOR M² | 42489.9337 | 4789.9619 | 0 | 4500.129 | 0 | 4789.9619 | 0 | 1795.2368 | 0 | 1779.5683 | 0 | 1795.2368 | 0 | 35904.735 | 0 | 33208.5605 | 0 | 35904.735 | 0
POT. Kt STOPING BASED ON TOT. RESOURCES | 90.271 | 23.2195 | 0 | 22 | 0 | 20.2777 | 0 | 18.2128 | 0 | 18.2 | 0 | 1.4709 | 0 | 48.8387 | 0 | 46.7 | 0 | 28.5781 | 0
POT. M² BASED ON TOT. RESOURCES | 21647.7197 | 5568.2172 | 0 | 5275.7794 | 0 | 4862.7689 | 0 | 4367.5762 | 0 | 4364.5084 | 0 | 352.7265 | 0 | 11711.9263 | 0 | 11199.0408 | 0 | 6853.2708 | 0
M/FLOW ALLOWED FOR STOPING FOR DESIGN WB | 531.5491 | 59.9224 | 0 | 56.2966 | 0 | 59.9224 | 0 | 22.4584 | 0 | 22.2624 | 0 | 22.4584 | 0 | 449.1682 | 0 | 415.4391 | 0 | 449.1682 | 0
M/FLOW ALLOWED FOR DEV. FOR DESIGN WB | 177.183 | 19.9741 | 0 | 18.7655 | 0 | 19.9741 | 0 | 7.4861 | 0 | 7.4208 | 0 | 7.4861 | 0 | 149.7227 | 0 | 138.4797 | 0 | 149.7227 | 0
ACTUAL TOTAL RESOURCES AVAIL. PER KILOTONNE | 744.5349 | 167.1642 |  | 158.3848 |  | 158.3848 | 0 | 278.1644 |  | 277.969 |  | 277.969 | 0 | 299.2064 |  | 286.1036 |  | 286.1036 | 0
Clear Sheet of all Information
Note on F3: Johan van Sittert: How much air do you require to mine the volume
Note on H3: Johan van Sittert: How much mining volume can you do with the air you have available
Note on L3: Johan van Sittert: How much air do you require to mine the volume
Note on N3: Johan van Sittert: How much mining volume can you do with the air you have available
Note on R3: Johan van Sittert: How much air do you require to mine the volume
Note on T3: Johan van Sittert: How much mining volume can you do with the air you have available
Note on D32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on E32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on F32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated of Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on G32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on H32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated of Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on I32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on J32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on K32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on L32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated of Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on M32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on N32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated of Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on O32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on P32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated from Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on Q32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on R32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated of Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on S32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on T32: (((Dist from #-1000)x((2.3xVRT)-59.5)/2500)+((6.833xVRT)-178)) Manupulated of Gebler Graph "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on U32: 3xHPR (Kw) - 3xTot Refr Avail (Kw) ÷ Massflow (Function 1 of formulae) Formula correct 5 Nov 2010
Note on D33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on E33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on F33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on G33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on H33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on I33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on J33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on K33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on L33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on M33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on N33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on O33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on P33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked J v Sittert
Note on Q33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on R33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on S33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on T33: =(-4*D28+120)/100 Manupulated of Gebler Graph Temp corection "y=mx+c" MSymons: Formula correct 5 Nov 2010 Checked H Nourse J v Sittert
Note on U33: 0.0533 x Depth below surface - 174.5 (Function 2 of formulae) Formula correct 5 Nov 2010
Note on D34: MSymons: formula correct Checked H Nourse J v Sittert
Note on E34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on F34: MSymons: formula correct Checked H Nourse J v Sittert
Note on G34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on H34: MSymons: formula correct Checked H Nourse J v Sittert
Note on I34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on J34: MSymons: formula correct Checked H Nourse J v Sittert
Note on K34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on L34: MSymons: formula correct Checked H Nourse J v Sittert
Note on M34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on N34: MSymons: formula correct Checked H Nourse J v Sittert
Note on O34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on P34: MSymons: formula correct Checked H Nourse J v Sittert
Note on Q34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on R34: MSymons: formula correct Checked H Nourse J v Sittert
Note on S34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on T34: MSymons: formula correct Checked H Nourse J v Sittert
Note on U34: -0.00125 x Depth below surface + 15.25 (Function 3 of formulae) Formula correct 5 Nov 2010
Note on D35: MSymons: formula correct Checked H Nourse J v Sittert
Note on F35: MSymons: formula correct Checked H Nourse J v Sittert
Note on H35: MSymons: formula correct Checked H Nourse J v Sittert
Note on J35: MSymons: formula correct Checked H Nourse J v Sittert
Note on L35: MSymons: formula correct Checked H Nourse J v Sittert
Note on N35: MSymons: formula correct Checked H Nourse J v Sittert
Note on P35: MSymons: formula correct Checked H Nourse J v Sittert
Note on R35: MSymons: formula correct Checked H Nourse J v Sittert
Note on T35: MSymons: formula correct Checked H Nourse J v Sittert
Note on D36: MSymons: formula correct Checked H Nourse J v Sittert
Note on F36: MSymons: formula correct Checked H Nourse J v Sittert
Note on H36: MSymons: formula correct Checked H Nourse J v Sittert
Note on J36: MSymons: formula correct Checked H Nourse J v Sittert
Note on L36: MSymons: formula correct Checked H Nourse J v Sittert
Note on N36: MSymons: formula correct Checked H Nourse J v Sittert
Note on P36: MSymons: formula correct Checked H Nourse J v Sittert
Note on R36: MSymons: formula correct Checked H Nourse J v Sittert
Note on T36: MSymons: formula correct Checked H Nourse J v Sittert
Note on D37: MSymons: formula correct Checked H Nourse J v Sittert
Note on F37: MSymons: formula correct Checked H Nourse J v Sittert
Note on H37: MSymons: formula correct Checked H Nourse J v Sittert
Note on J37: MSymons: formula correct Checked H Nourse J v Sittert
Note on L37: MSymons: formula correct Checked H Nourse J v Sittert
Note on N37: MSymons: formula correct Checked H Nourse J v Sittert
Note on P37: MSymons: formula correct Checked H Nourse J v Sittert
Note on R37: MSymons: formula correct Checked H Nourse J v Sittert
Note on T37: MSymons: formula correct Checked H Nourse J v Sittert
Note on E38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on G38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on I38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on K38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on M38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on O38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on Q38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on S38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on U38: Heat Removal Capacity of air (WITH BAC Operating) =(Design Reject -26)x(-0.00125xDepth below surface+15.25)/3-0.01775xDepth below surface+58.25 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 5 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on E39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on G39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on I39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on K39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on M39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on O39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on Q39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on S39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on U39: Heat Removal Capacity of air (WITHOUT BAC Operating) =(Design Reject -26)x(-0.0026xDepth below surface+20.1)/3-0.015xDepth below surface+30 Manupulated from Heat Removal Graph "y=mx+c" Formula correct 8 Nov 2010 MSymons: formula correct Checked J v Sittert
Note on D40: Formula correct Checked H Nourse J v Sittert
Note on E40: To get to 1000 / sec per 24 shifts
Note on F40: Formula correct Checked H Nourse J v Sittert
Note on G40: To get to 1000 / sec per 24 shifts
Note on H40: Formula correct Checked H Nourse J v Sittert
Note on I40: To get to 1000 / sec per 24 shifts
Note on J40: Formula correct Checked H Nourse J v Sittert
Note on K40: To get to 1000 / sec per 24 shifts
Note on L40: Formula correct Checked H Nourse J v Sittert
Note on M40: To get to 1000 / sec per 24 shifts
Note on N40: Formula correct Checked H Nourse J v Sittert
Note on O40: To get to 1000 / sec per 24 shifts
Note on P40: Formula correct Checked H Nourse J v Sittert
Note on Q40: To get to 1000 / sec per 24 shifts
Note on R40: Formula correct Checked H Nourse J v Sittert
Note on S40: To get to 1000 / sec per 24 shifts
Note on T40: Formula correct Checked H Nourse J v Sittert
Note on U40: To get to 1000 / sec per 24 shifts
Note on D42: Formula correct Checked H Nourse J v Sittert
Note on F42: Formula correct Checked H Nourse J v Sittert
Note on H42: Formula correct Checked H Nourse J v Sittert
Note on J42: Formula correct Checked H Nourse J v Sittert
Note on L42: Formula correct Checked H Nourse J v Sittert
Note on N42: Formula correct Checked H Nourse J v Sittert
Note on P42: Formula correct Checked H Nourse J v Sittert
Note on R42: Formula correct Checked H Nourse J v Sittert
Note on T42: Formula correct Checked H Nourse J v Sittert
Note on D43: Formula correct Checked H Nourse J v Sittert
Note on E43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on F43: Formula correct Checked H Nourse J v Sittert
Note on G43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on H43: Formula correct Checked H Nourse J v Sittert
Note on I43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on J43: Formula correct Checked H Nourse J v Sittert
Note on K43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on L43: Formula correct Checked H Nourse J v Sittert
Note on M43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on N43: Formula correct Checked H Nourse J v Sittert
Note on O43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on P43: Formula correct Checked H Nourse J v Sittert
Note on Q43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on R43: Formula correct Checked H Nourse J v Sittert
Note on S43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on T43: Formula correct Checked H Nourse J v Sittert
Note on U43: 0.045 x Depth below surface-90 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on D44: Formula correct Checked H Nourse J v Sittert
Note on E44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on F44: Formula correct Checked H Nourse J v Sittert
Note on G44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on H44: Formula correct Checked H Nourse J v Sittert
Note on I44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on J44: Formula correct Checked H Nourse J v Sittert
Note on K44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on L44: Formula correct Checked H Nourse J v Sittert
Note on M44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on N44: Formula correct Checked H Nourse J v Sittert
Note on O44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on P44: Formula correct Checked H Nourse J v Sittert
Note on Q44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on R44: Formula correct Checked H Nourse J v Sittert
Note on S44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on T44: Formula correct Checked H Nourse J v Sittert
Note on U44: =-0.0026 x Depth below surface+20.1 (Function 2 of formulae NO BAC) Formula correct 8 Nov 2010
Note on E49: Formula correct Density of air Checked H Nourse J v Sittert
Note on G49: Formula correct Density of air Checked H Nourse J v Sittert
Note on I49: Formula correct Density of air Checked H Nourse J v Sittert
Note on K49: Formula correct Density of air Checked H Nourse J v Sittert
Note on M49: Formula correct Density of air Checked H Nourse J v Sittert
Note on O49: Formula correct Density of air Checked H Nourse J v Sittert
Note on Q49: Formula correct Density of air Checked H Nourse J v Sittert
Note on S49: Formula correct Density of air Checked H Nourse J v Sittert
Note on U49: Formula correct Density of air Checked H Nourse J v Sittert
Note on D52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on F52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on H52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on J52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on L52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on N52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on P52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on R52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on T52: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.0533 x Depth below surface - 174.5) ÷ ((-0.00125xDepth below surface)+15.25) + 26 Formula correct 5 Nov 2010
Note on D54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on F54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on H54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on J54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on L54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on N54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on P54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on R54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010
Note on T54: ((3xHPRKw - 3xTot Refr AvailKw)) ÷ Massflow) + (0.045 x Depth below surface - 90) ÷ ((-0.0026xDepth below surface)-20.1) + 26 Formula correct 8 Nov 2010